## Pump Station
1. Inputs
Energy required | 60 | MW
Operation off-peak | 10 | hr/day
Operation on-peak | 10 | hr/day
Off peak electrcial costs | 13.27 | $/MWhr
On peak electrical | 19 | $/MWhr
Operation | 365 | day/yr
Life | 30 | years
Energy inflation | 5%
Maintenance inflation | 4%
Discount Rate | 6%
Energy | Efficiency
Existing | 89.7%
New | 91.5%
Maintenance activities | Frequency |  | Cost
Minor repairs | 4 | months | 325000
Major repairs | 12 | months | 1300000
Annual maintenance | 975012
Major rejuvenation (new) | 20%
Major rejuvenation (old) | 55%
2. Alternative: Refurbish existing pumps
| Pumping requirements | Offpeak pumping | On-peak pumping | Off-peak time | On-peak time | Off-peak Energy costs | On-peak Energy costs | Regular Maintenance | Refurbish | Total cost | Discount factor | PV(Energy Costs)
Year
0 | 117 | 117 | 0 | 10 | 0 |  | 0 |  | -22600 | -22600 | 1 | -22600
1 | 120.9 | 117 | 3.9 | 10 | 0.33333 | -3401.8244 | -162.3579 | -1014.0125 |  | -4578.1948 | 0.9434 | -4319.0517
2 | 124.8 | 117 | 7.8 | 10 | 0.66667 | -3571.9156 | -340.9515 | -1054.573 |  | -4967.4401 | 0.89 | -4421.004
3 | 128.7 | 117 | 11.7 | 10 | 1 | -3750.5114 | -536.9986 | -1096.7559 |  | -5384.2659 | 0.83962 | -4520.7335
4 | 132.6 | 117 | 15.6 | 10 | 1.3333 | -3938.037 | -751.7981 | -1140.6261 |  | -5830.4612 | 0.79209 | -4618.2714
5 | 136.5 | 117 | 19.5 | 10 | 1.6667 | -4134.9388 | -986.735 | -1186.2512 | -15122.9956 | -21430.9206 | 0.74726 | -16014.4305
6 | 140.4 | 117 | 23.4 | 10 | 2 | -4341.6858 | -1243.2861 | -1233.7012 |  | -6818.6731 | 0.70496 | -4806.8954
7 | 144.3 | 117 | 27.3 | 10 | 2.3333 | -4558.7701 | -1523.0254 | -1283.0493 |  | -7364.8448 | 0.66506 | -4898.0424
8 | 148.2 | 117 | 31.2 | 10 | 2.6667 | -4786.7086 | -1827.6305 | -1334.3712 |  | -7948.7103 | 0.62741 | -4987.1192
9 | 152.1 | 117 | 35.1 | 10 | 3 | -5026.044 | -2158.8885 | -1387.7461 |  | -8572.6786 | 0.5919 | -5074.1553
10 | 156 | 117 | 39 | 10 | 3.3333 | -5277.3462 | -2518.7033 | -1443.2559 | -18399.4365 | -27638.7419 | 0.55839 | -15433.3291
11 | 159.9 | 117 | 42.9 | 10 | 3.6667 | -5541.2135 | -2909.1023 | -1500.9862 |  | -9951.302 | 0.52679 | -5242.2217
12 | 163.8 | 117 | 46.8 | 10 | 4 | -5818.2742 | -3332.2444 | -1561.0256 |  | -10711.5443 | 0.49697 | -5323.3093
13 | 167.7 | 117 | 50.7 | 10 | 4.3333 | -6109.1879 | -3790.4281 | -1623.4667 |  | -11523.0826 | 0.46884 | -5402.4708
14 | 171.6 | 117 | 54.6 | 10 | 4.6667 | -6414.6473 | -4286.0994 | -1688.4053 |  | -12389.152 | 0.4423 | -5479.7339
15 | 175.5 | 117 | 58.5 | 10 | 5 | -6735.3797 | -4821.8618 | -1755.9415 | -22385.7278 | -35698.9108 | 0.41727 | -14895.9082
16 | 179.4 | 117 | 62.4 | 10 | 5.3333 | -7072.1486 | -5400.4853 | -1826.1792 |  | -14298.8131 | 0.39365 | -5628.6746
17 | 183.3 | 117 | 66.3 | 10 | 5.6667 | -7425.7561 | -6024.9164 | -1899.2264 |  | -15349.8988 | 0.37136 | -5700.4062
18 | 187.2 | 117 | 70.2 | 10 | 6 | -7797.0439 | -6698.2894 | -1975.1954 |  | -16470.5287 | 0.35034 | -5770.3475
19 | 191.1 | 117 | 74.1 | 10 | 6.3333 | -8186.8961 | -7423.9374 | -2054.2032 |  | -17665.0367 | 0.33051 | -5838.5245
20 | 195 | 117 | 78 | 10 | 6.6667 | -8596.2409 | -8205.4045 | -2136.3714 | -27235.6607 | -46173.6774 | 0.3118 | -14397.1709
21 | 198.9 | 117 | 81.9 | 10 | 7 | -9026.0529 | -9046.4585 | -2221.8262 |  | -20294.3376 | 0.29416 | -5969.689
22 | 202.8 | 117 | 85.8 | 10 | 7.3333 | -9477.3556 | -9951.1043 | -2310.6993 |  | -21739.1591 | 0.27751 | -6032.7275
23 | 206.7 | 117 | 89.7 | 10 | 7.6667 | -9951.2233 | -10923.5986 | -2403.1272 |  | -23277.9492 | 0.2618 | -6094.1033
24 | 210.6 | 117 | 93.6 | 10 | 8 | -10448.7845 | -11968.4645 | -2499.2523 |  | -24916.5014 | 0.24698 | -6153.8413
25 | 214.5 | 117 | 97.5 | 10 | 8.3333 | -10971.2237 | -13090.5081 | -2599.2224 | -33136.3456 | -59797.2998 | 0.233 | -13932.689
26 | 218.4 | 117 | 101.4 | 10 | 8.6667 | -11519.7849 | -14294.8348 | -2703.1913 |  | -28517.8111 | 0.21981 | -6268.5009
27 | 222.3 | 117 | 105.3 | 10 | 9 | -12095.7742 | -15586.868 | -2811.319 |  | -30493.9611 | 0.20737 | -6323.4703
28 | 226.2 | 117 | 109.2 | 10 | 9.3333 | -12700.5629 | -16972.3674 | -2923.7717 |  | -32596.7019 | 0.19563 | -6376.8975
29 | 230.1 | 117 | 113.1 | 10 | 9.6667 | -13335.591 | -18457.4495 | -3040.7226 |  | -34833.7631 | 0.18456 | -6428.8057
30 | 234 | 117 | 117 | 10 | 10 | -14002.3706 | -20048.6089 | -3162.3515 |  | -37213.331 | 0.17411 | -6479.2179
[9 empty] | EAC | -17103.8598 | NPV | -235431.7425
3. Alternative 2: Install new pumps
New pumps | Pumping requirements | Offpeak pumping | On-peak pumping | Off-peak time | On-peak time | Off-peak Energy costs | On-peak Energy costs | Regular Maintenance | New And Major maintenance |  | Discount factor | PV(Energy Costs)
Year
0 | 117 | 117 | 0 | 10 | 0 |  | 0 |  | -32600 | -32600 | 1 | -32600
1 | 120.9 | 117 | 3.9 | 10 | 0.33333 | -3334.9033 | -162.3579 | -1014.0125 |  | -4511.2736 | 0.9434 | -4255.9185
2 | 124.8 | 117 | 7.8 | 10 | 0.66667 | -3501.6484 | -340.9515 | -1054.573 |  | -4897.1729 | 0.89 | -4358.4665
3 | 128.7 | 117 | 11.7 | 10 | 1 | -3676.7309 | -536.9986 | -1096.7559 |  | -5310.4854 | 0.83962 | -4458.7859
4 | 132.6 | 117 | 15.6 | 10 | 1.3333 | -3860.5674 | -751.7981 | -1140.6261 |  | -5752.9916 | 0.79209 | -4556.9082
5 | 136.5 | 117 | 19.5 | 10 | 1.6667 | -4053.5958 | -986.735 | -1186.2512 |  | -6226.5819 | 0.74726 | -4652.8642
6 | 140.4 | 117 | 23.4 | 10 | 2 | -4256.2756 | -1243.2861 | -1233.7012 |  | -6733.2629 | 0.70496 | -4746.6846
7 | 144.3 | 117 | 27.3 | 10 | 2.3333 | -4469.0893 | -1523.0254 | -1283.0493 |  | -7275.164 | 0.66506 | -4838.3996
8 | 148.2 | 117 | 31.2 | 10 | 2.6667 | -4692.5438 | -1827.6305 | -1334.3712 |  | -7854.5456 | 0.62741 | -4928.0391
9 | 152.1 | 117 | 35.1 | 10 | 3 | -4927.171 | -2158.8885 | -1387.7461 |  | -8473.8056 | 0.5919 | -9860.9598
10 | 156 | 117 | 39 | 10 | 3.3333 | -5173.5296 | -2518.7033 | -1443.2559 | -9651.1927 | -18786.6815 | 0.55839 | -29880.5718
11 | 159.9 | 117 | 42.9 | 10 | 3.6667 | -5432.206 | -2909.1023 | -1500.9862 |  | -9842.2945 | 0.52679 | -5184.798
12 | 163.8 | 117 | 46.8 | 10 | 4 | -5703.8163 | -3332.2444 | -1561.0256 |  | -10597.0864 | 0.49697 | -5266.4273
13 | 167.7 | 117 | 50.7 | 10 | 4.3333 | -5989.0071 | -3790.4281 | -1623.4667 |  | -11402.9019 | 0.46884 | -5346.1254
14 | 171.6 | 117 | 54.6 | 10 | 4.6667 | -6288.4575 | -4286.0994 | -1688.4053 |  | -12262.9622 | 0.4423 | -9692.6519
15 | 175.5 | 117 | 58.5 | 10 | 5 | -6602.8804 | -4821.8618 | -1755.9415 |  | -13180.6838 | 0.41727 | -5499.8388
16 | 179.4 | 117 | 62.4 | 10 | 5.3333 | -6933.0244 | -5400.4853 | -1826.1792 |  | -14159.6889 | 0.39365 | -5573.9089
17 | 183.3 | 117 | 66.3 | 10 | 5.6667 | -7279.6756 | -6024.9164 | -1899.2264 |  | -15203.8184 | 0.37136 | -5646.1572
18 | 187.2 | 117 | 70.2 | 10 | 6 | -7643.6594 | -6698.2894 | -1975.1954 |  | -16317.1442 | 0.35034 | -5716.6102
19 | 191.1 | 117 | 74.1 | 10 | 6.3333 | -8025.8424 | -7423.9374 | -2054.2032 |  | -17503.983 | 0.33051 | -5785.2941
20 | 195 | 117 | 78 | 10 | 6.6667 | -8427.1345 | -8205.4045 | -2136.3714 | -14286.1229 | -33055.0332 | 0.3118 | -10306.7156
21 | 198.9 | 117 | 81.9 | 10 | 7 | -8848.4912 | -9046.4585 | -2221.8262 |  | -20116.7759 | 0.29416 | -5917.4583
22 | 202.8 | 117 | 85.8 | 10 | 7.3333 | -9290.9158 | -9951.1043 | -2310.6993 |  | -21552.7193 | 0.27751 | -5980.9895
23 | 206.7 | 117 | 89.7 | 10 | 7.6667 | -9755.4616 | -10923.5986 | -2403.1272 |  | -23082.1874 | 0.2618 | -6042.8534
24 | 210.6 | 117 | 93.6 | 10 | 8 | -10243.2346 | -11968.4645 | -2499.2523 |  | -24710.9515 | 0.24698 | -6103.0749
25 | 214.5 | 117 | 97.5 | 10 | 8.3333 | -10755.3964 | -13090.5081 | -2599.2224 |  | -26445.1269 | 0.233 | -6161.6783
26 | 218.4 | 117 | 101.4 | 10 | 8.6667 | -11293.1662 | -14294.8348 | -2703.1913 |  | -28291.1923 | 0.21981 | -6218.6878
27 | 222.3 | 117 | 105.3 | 10 | 9 | -11857.8245 | -15586.868 | -2811.319 |  | -30256.0115 | 0.20737 | -6274.1271
28 | 226.2 | 117 | 109.2 | 10 | 9.3333 | -12450.7157 | -16972.3674 | -2923.7717 |  | -32346.8548 | 0.19563 | -6328.0198
29 | 230.1 | 117 | 113.1 | 10 | 9.6667 | -13073.2515 | -18457.4495 | -3040.7226 |  | -34571.4236 | 0.18456 | -6380.3892
30 | 234 | 117 | 117 | 10 | 10 | -13726.9141 | -20048.6089 | -3162.3515 |  | -36937.8745 | 0.17411 | -6431.2582
[9 empty] | EAC | -17072.1064 | NPV | -234994.6621
4. Sensitivity Analysis
| Existing-New |  | Decision |  |  | Decision |  |  | Decision
Discount Rate | -0.43708 |  | New | Maintenance inflation | -0.43708 | New | Energy inflation | -0.43708 | New
0% | -64.6576 |  | New | 0% | 7.1788 | Existing | 0% | -1.9973 | New
2% | -34.9577 |  | New | 2% | 4.2102 | Existing | 2% | -1.4123 | New
4% | -14.6659 |  | New | 3.845% | -6.7235e-05 | New | 4% | -0.77201 | New
6.074% | 0.0004429 |  | Existing | 6% | -7.6449 | New | 6.287% | -5.4181e-05 | New
8% | 9.7958 |  | Existing | 8% | -18.7201 | New | 8% | 0.57094 | Existing
10% | 17.3344 |  | Existing | 10% | -35.5875 | New | 10% | 1.1628 | Existing
12% | 23.0149 |  | Existing | 12% | -61.0659 | New | 12% | 1.5606 | Existing