- PART I - GENERAL

- 1.01	RELATED DOCUMENTS

- A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

- 1.02	SUMMARY

- A.	This Section includes the following utility materials and methods to complement other Division 2 Sections:

          - Piping materials and installation instructions common to most piping systems.

          - Concrete base construction requirements.

          - Equipment nameplate data requirements.

          - Non-shrink grout for equipment installations.

          - Field-fabricated metal and wood equipment supports.

          - Utility piping demolition.

          - Cutting and patching.

          - Touchup painting and finishing.

        - Pipe and pipe fitting materials are specified in Division 2 piping Sections.

        - Related Sections include the following:

          - Division 2 Section "Earthwork" for excavating, trenching, and backfilling.

          - Division 3 Section "Cast-in-Place Concrete" for bases and thrust restraints.

- 1.03	DEFINITIONS

- A.	Exposed Installations: Exposed to view outdoors, or subject to outdoor ambient temperatures and weather conditions.

- B.	Concealed Installations: Concealed from view and protected from weather conditions and physical contact by building occupants, but subject to outdoor ambient temperatures.  Examples include installations within unheated shelters.

- C.	The following are industry abbreviations for plastic materials:

- 1.	ABS:  Acrylonitrile-butadiene-styrene.

- 2.	CPVC:  Chlorinated polyvinyl chloride.

- 3.	PE:  Polyethylene.

- 4.	PVC:  Polyvinyl chloride.

- 1.04	SUBMITTALS

- A.	Product Data: For identification materials and devices.

- B.	Samples of color, lettering styles, and other graphic representation required for each identification material and device.

- C.	Shop Drawings: Detail fabrication and installation for metal and wood supports, and anchorage for utility piping materials and equipment.

- D.	Coordination Drawings: Detail major elements, components, and systems of utility equipment and materials in relation to other systems, installations, and building components.  Show space requirements for installation and access.  Indicate whether sequence and coordination of installations are important to efficient flow of the Work.  Include the following:

- 1.	Planned piping layout, including valve and specialty locations and valve-stem movement.

- 2.	Clearances for installing and maintaining insulation.

- 3.	Clearances for servicing and maintaining equipment, accessories, and specialties, including space for disassembly required for periodic maintenance.

- 4.	Equipment and accessory service connections and support details.

- 5.	Building, exterior wall, and foundation penetrations.

- 6.	Sizes and location of required concrete bases.

- 7.	Scheduling, sequencing, movement, and positioning of large equipment during construction.

- 8.	Floor plans, elevations, and details to indicate penetrations in floors and walls, and their relationship to other penetrations and installations.

- E.	Welding Certificates: Copies of certificates indicating compliance of welding procedures and personnel with requirements specified in the "Quality Assurance" Article of this Section.

- 1.05	QUALITY ASSURANCE

- A.	Qualify welding processes and operators for structural steel according to AWS D1.1, "Structural Welding Code--Steel."

- B.	Qualify welding processes and operators for piping according to the ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications."

- 1.	Comply with provisions of ASME B31 Series, "Code for Pressure Piping."

- 2.	Certify that each welder has passed AWS qualification tests for welding processes involved and that certification is current.

- C.	Comply with ASME A13.1 for lettering size, length of color field, colors, and viewing angles of identification devices.

- D.	Equipment Selection: Equipment of greater or larger power, dimensions, capacities, and ratings may be furnished provided such proposed equipment is approved in writing and connecting mechanical and electrical services, circuit breakers, conduit, motors, bases, and equipment spaces are increased.  If larger equipment is approved, no additional costs will be approved for these increases.  If minimum energy ratings or efficiencies of equipment are specified, equipment must meet design requirements and commissioning requirements.

- 1.06	DELIVERY, STORAGE, AND HANDLING

- A.	Deliver pipes and tubes with factory-applied end caps.  Maintain end caps through shipping, storage, and handling to prevent pipe-end damage and entrance of dirt, debris, and moisture.

- B.	Protect stored pipes and tubes from moisture and dirt.  Elevate above grade.  Do not exceed structural capacity of floor, if stored inside.

- C.	Protect flanges, fittings, and piping specialties from moisture and dirt.

- D.	Store plastic pipes protected from direct sunlight.  Support to prevent sagging and bending.

- 1.07	SEQUENCING AND SCHEDULING

- A.	Coordinate equipment installation with other components.

- B.	Coordinate installation of required supporting devices and set sleeves in poured-in-place concrete and other structural components as they are constructed.

- C.	Sequence, coordinate, and integrate installations of materials and equipment for efficient flow of the Work.

- D.	Coordinate connection of piping systems with other exterior underground and overhead utilities and services.  Comply with requirements of authorities having jurisdiction, franchised service companies, and controlling agencies.

- E.	Coordinate installation of identifying devices after completing covering and painting, if devices are applied to surfaces.

- PART II - PRODUCTS

- 2.01	PIPE AND PIPE FITTINGS

- A.	Refer to individual Division 2 Sections for pipe and fitting materials and joining methods.

- B.	Pipe Threads: ASME B1.20.1 for factory-threaded pipe and pipe fittings.

- 2.02	JOINING MATERIALS

- A.	Refer to individual Division 2 piping Sections for special joining materials not listed below.

- B.	Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.

- 1.	ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness, unless otherwise indicated.

            - Full-Face Type: For flat-face, Class 125 cast-iron and cast-bronze flanges.

            - Narrow-Face Type: For raised-face, Class 250 cast-iron and steel flanges.

- 2.	AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick, unless otherwise indicated; and full-face or ring type, unless otherwise indicated.

- C.	Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.

- D.	Plastic Pipe-Flange Gasket, Bolts, and Nuts: Type and material recommended by piping system manufacturer, unless otherwise indicated.

- E.	Solder Filler Metal: ASTM B 32.

- 1.	Alloy Sn95 or Alloy Sn94: Approximately 95 percent tin and 5 percent silver, with 0.10 percent lead content.

- 2.	Alloy E: Approximately 95 percent tin and 5 percent copper, with 0.10 percent maximum lead content.

- 3.	Alloy HA: Tin-antimony-silver-copper zinc, with 0.10 percent maximum lead content.

- 4.	Alloy HB: Tin-antimony-silver-copper nickel, with 0.10 percent maximum lead content.

- 5.	Alloy Sb5: 95 percent tin and 5 percent antimony, with 0.20 percent maximum lead content.

- F.	Brazing Filler Metals: AWS A5.8.

- 1.	BCuP Series: Copper-phosphorus alloys.

- 2.	BAg1:  Silver alloy.

- G.	Welding Filler Metals: Comply with AWS D10.12 for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

- H.	Solvent Cements: Manufacturer’s standard solvent cements for the following:

- 1.	ABS Plastic Piping ASTM D 2235.

- 2.	CPVC Plastic Piping: ASTM F 493.

- 3.	PVC Plastic Piping: ASTM D 2564.  Include primer according to ASTM F 656.

- 4.	ABS to PVC Plastic Piping Transition: ASTM D 3138.

- I.	Plastic Pipe Seals: ASTM F 477, elastomeric gasket.

- J.	Flanged, Ductile-Iron-Pipe Gaskets, Bolts, and Nuts: AWWA C110, rubber gasket, carbon-steel bolts and nuts.

- K.	Couplings:  Iron-body sleeve assembly, fabricated to match OD of plain-end, pressure pipes.

- 1.	Sleeve:  ASTM A 126, Class B, gray iron.

- 2.	Followers:  ASTM A 47 (ASTM A 47M) malleable iron or ASTM A 536 ductile iron.

- 3.	Gaskets:  Rubber.

- 4.	Bolts and Nuts: AWWA C111.

- 5.	Finish:  Enamel paint.

- 2.03	PIPING SPECIALTIES

- A.	Dielectric Fittings: Assembly or fitting with insulating material isolating joined dissimilar metals, to prevent galvanic action and to stop corrosion.

- 1.	Description:  Combination of copper alloy and ferrous; threaded, solder, plain, and weld neck end types; and matching piping system materials.

- 2.	Insulating Material: Suitable for system fluid, pressure, and temperature.

- 3.	Dielectric Unions: Factory-fabricated union assembly, for 250-psig (1725-kPa) minimum working pressure at 180 degrees F (82 degrees C).

- 4.	Dielectric Flanges: Factory-fabricated, companion-flange assembly, for 150- or 300-psig (1035- or 2070-kPa) minimum working pressure as required to suit system pressures.

- 5.	Dielectric-Flange Insulation Kits: Field-assembled, companion-flange assembly, full-face or ring type.  Components include neoprene or phenolic gasket, phenolic or PE bolt sleeves, phenolic washers, and steel backing washers.

- a.	Provide separate companion flanges and steel bolts and nuts for 150- or 300-psig (1035- or 2070-kPa) minimum working pressure as required to suit system pressures.

- 6.	Dielectric Couplings: Galvanized-steel coupling; with inert and non-corrosive, thermoplastic lining; threaded ends; and 300-psig (2070-kPa) minimum working pressure at 225 degrees F (107 degrees C).

- 7.	Dielectric Nipples: Electroplated steel nipple; with inert and non-corrosive, thermoplastic lining; plain, threaded, or grooved ends; and 300-psig (2070-kPa) minimum working pressure at 225 degrees F (107 degrees C).

- B.	Sleeves:  The following materials are for wall, floor, slab, and roof penetrations:

- 1.	Steel Sheet Metal: 0.0239-inch (0.6-mm) minimum thickness, galvanized, round tube closed with welded longitudinal joint.

- 2.	Steel Pipe: ASTM A 53, Type E, Grade A, Schedule 40, galvanized, plain ends.

- 3.	Cast Iron: Cast or fabricated wall pipe equivalent to ductile iron pressure pipe, with plain ends and integral water stop, unless otherwise indicated.

- 4.	PVC Plastic: Manufactured, permanent, with nailing flange for attaching to wooden forms.

- 5.	PVC Plastic Pipe: ASTM D 1785, Schedule 40.

- 6.	PE Plastic: Manufactured, reusable, tapered, cup-shaped, smooth outer surface with nailing flange for attaching to wooden forms.

- 2.04	IDENTIFYING DEVICES AND LABELS

- A.	General:  Manufacturer's standard products of categories and types required for each application as referenced in other Division 2 Sections.  If more than one type is specified for application, selection is Installer's option, but provide one selection for each product category.

- B.	Equipment Nameplates: Metal nameplate with operational data engraved or stamped; permanently fastened to equipment.

- 1.	Data:  Manufacturer, product name, model number, serial number, capacity, operating and power characteristics, labels of tested compliances, and similar essential data.

- 2.	Location:  An accessible and visible location.

- C.	Stencils: Standard stencils, prepared for required applications with letter sizes complying with recommendations of ASME A13.1 for piping and similar applications, but at least 1-1/4-inch- (30-mm-) high letters for ductwork and at least 3/4-inch- (19-mm-) high letters for access door signs and similar operational instructions.

- 1.	Material:  Fiberboard.

- 2.	Material:  Brass.

- 3.	Stencil Paint: Standard exterior-type stenciling enamel; black, unless otherwise indicated; either brushing grade or pressurized spray-can form and grade.

- 4.	Identification Paint: Standard identification enamel of colors indicated or, if not otherwise indicated for piping systems, comply with ASME A13.1 for colors.

- D.	Pressure-Sensitive Pipe Markers: Manufacturer's standard preprinted, permanent-adhesive, color-coded, pressure-sensitive vinyl, complying with ASME A13.1.

- E.	Plastic Duct Markers: Manufacturer’s standard color-coded laminated plastic.  Comply with the following color-codes:

- 1.	Green:  Cold air.

- 2.	Yellow:  Hot air.

- 3.	Yellow/Green or Green: Supply air.

- 4.	Blue:  Exhaust, outside, return, and mixed air.

- 5.	For hazardous exhausts, use colors and designs recommended by ASME A13.1.

- 6.	Nomenclature:  Include the following:

- a.	Direction of airflow.

- b.	Duct service.

- c.	Duct origin.

- d.	Duct destination.

- e.	Design cubic feet/minute (Liters/second).

- F.	Engraved Plastic-Laminate Signs: ASTM D 709, Type I, cellulose, paper-base, phenolic-resin-laminate engraving stock; Grade ES-2, black surface, black phenolic core, with white melamine sub-core, unless otherwise indicated.

- 1.	Fabricate in sizes required for message.

- 2.	Engraved with engraver's standard letter style, of sizes and with wording to match equipment identification.

- 3.	Punch for mechanical fastening.

- 4.	Thickness:  1/16 inch (1.6 mm), unless otherwise indicated.

- 5.	Thickness:  1/8 inch (3.2 mm), unless otherwise indicated.

- 6.	Thickness:  1/16 inch (1.6 mm), for units up to 20 sq. in. (130 sq. cm) or 8 inches (200 mm) long; 1/8 inch (3.2 mm) for larger units.

- 7.	Fasteners:  Self-tapping stainless-steel screws or contact-type permanent adhesive.

- G.	Plastic Equipment Markers: Color-coded laminated plastic.  Comply with the following color-codes:

- 1.	Green:  Cooling equipment and components.

- 2.	Yellow:  Heating equipment and components.

- 3.	Yellow/Green: Combination cooling and heating equipment and components.

- 4.	Brown:  Energy reclamation equipment and components.

- 5.	Blue:  Equipment and components that do not meet any criteria above.

- 6.	For hazardous equipment, use colors and designs recommended by ASME A13.1.

- 7.	Nomenclature:  Include the following, matching terminology on schedules as closely as possible:

- a.	Name and plan number.

- b.	Equipment service.

- c.	Design capacity.

- d.	Other design parameters such as pressure drop, entering and leaving conditions, and revolutions/minute.

- 8.	Size:  Approximate 2-1/2 by 4 inches (65 by 100 mm) for control devices, dampers, and valves; and 4-1/2 by 6 inches (115 by 150 mm) for equipment.

- H.	Lettering and Graphics: Coordinate names, abbreviations, and other designations used in mechanical identification with corresponding designations indicated.  Use numbers, lettering, and wording indicated for proper identification and operation/maintenance of mechanical systems and equipment.

- 1.	Multiple Systems: If multiple systems of same generic name are indicated, provide identification that indicates individual system number and service.

- 2.05	GROUT

- A.	Non-shrink, Non-metallic Grout: ASTM C 1107, Grade B.

- 1.	Characteristics:  Post-hardening, volume-adjusting, dry, hydraulic-cement grout; non-staining; non-corrosive; non-gaseous; and recommended for interior and exterior applications.

- 2.	Design Mix: 5000 psig (34.5 MPa), 28-day compressive strength.

- 3.	Packaging:  Premixed and factory packaged.

- PART III - EXECUTION

- 3.01	PIPING SYSTEMS - COMMON REQUIREMENTS

- A.	General:  Install piping as described below, unless piping Sections specify otherwise.  Individual Division 2 piping Sections specify unique piping installation requirements.

- B.	General Locations and Arrangements: Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated, unless deviations to layout are approved on Coordination Drawings.

- C.	Install piping at indicated slopes.

- D.	Install components with pressure rating equal to or greater than system operating pressure.

- E.	Install piping free of sags and bends.

- F.	Install exposed interior and exterior piping at right angles or parallel to building walls.  Diagonal runs are prohibited, unless otherwise indicated.

- G.	Locate groups of pipes parallel to each other, spaced to permit valve servicing.

- H.	Install fittings for changes in direction and branch connections.

- I.	Install couplings according to manufacturer's written instructions.

- J.	Sleeves are not required for core drilled holes.

- K.	Permanent sleeves are not required for holes formed by PE plastic removable sleeves.

- L.	Verify final equipment locations for roughing-in.

- M.	Refer to equipment specifications in other Division 2 Sections for roughing-in requirements.

- N.	Piping Joint Construction: Join pipe and fittings as follows and as specifically required in individual piping Sections:

- 1.	Remove scale, slag, dirt, and debris from inside and outside pipe and fittings before assembly.

- 2.	Remove scale, slag, dirt, and debris from inside and outside pipe and fittings before assembly.

- 3.	Soldered Joints: Construct joints according to AWS's "Soldering Manual," Chapter "The Soldering of Pipe and Tube"; or CDA's "Copper Tube Handbook."

- 4.	Soldered Joints: Construct joints according to AWS's "Soldering Manual," Chapter "The Soldering of Pipe and Tube."

- 5.	Soldered Joints: Construct joints according to CDA’s “Copper Tube Handbook”.

- 6.	Brazed Joints: Construct joints according to AWS's "Brazing Handbook," Chapter "Pipe and Tube."

- 7.	Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

- a.	Note internal length of threads in fittings or valve ends, and proximity of internal seat or wall, to determine how far pipe should be threaded into joint.

- b.	Apply appropriate tape or thread compound to external pipe threads, unless dry seal threading is specified.

- c.	Align threads at point of assembly.

- d.	Tighten joint with wrench.  Apply wrench to valve end into which pipe is being threaded.

- e.	Damaged Threads: Do not use pipe or pipe fittings with corroded or damaged threads.  Do not use pipe sections that have cracked or open welds.

- 8.	Welded Joints: Construct joints according to AWS D10.12, “recommended Practices and Procedures for Welding Low Carbon Steel Pipe," using qualified processes and welding operators according to "Quality Assurance" Article.

- 9.	Flanged Joints: Align flange surfaces parallel.  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Assemble joints by sequencing bolt tightening to make initial contact of flanges and gaskets as flat and parallel as possible.  Use suitable lubricants on bolt threads.  Tighten bolts gradually and uniformly using torque wrench.

- 10.	Plastic Piping Solvent-Cement Joints: Clean and dry joining surfaces by wiping with clean cloth or paper towels.  Join pipe and fittings according to the following:

- a.	Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

- b.	ABS Plastic Piping: ASTM D 2235 and ASTM D 2661.

- c.	CPVC Plastic Piping:  ASTM D 2846 and ASTM F 493.

- d.	PVC Plastic, Pressure Piping: ASTM D 2672.

- e.	PVC Plastic, Non-pressure Piping: ASTM D 2855.

- f.	ABS to PVC Plastic, Non-pressure Transition Fittings: Procedure and solvent cement according to ASTM D 3138.

- 11.	Plastic Piping Heat-Fusion Joints: Clean and dry joining surfaces by wiping with clean cloth or paper towels.  Join according to ASTM D 2657 procedures and manufacturers’ written instructions.

- a.	Plain-End Pipe and Fittings: Use butt fusion.

- b.	Plain-End Pipe and Socket Fittings: Use socket fusion.

- O.	Piping Connections: Make connections according to the following, unless otherwise indicated:

- 1.	Install unions, in piping 2-inch NPS (DN50) and smaller, adjacent to each valve and at final connection to each piece of equipment with 2-inch NPS (DN50) or smaller threaded pipe connection.

- 2.	Install flanges, in piping 2-1/2-inch NPS (DN65) and larger, adjacent to flanged valves and at final connection to each piece of equipment with flanged pipe connection.

- 3.	Dry Piping Systems: Install dielectric unions and flanges to connect piping materials of dissimilar metals.

- 4.	Wet Piping Systems: Install dielectric coupling and nipple fittings to connect piping materials of dissimilar metals.

- 3.02	EQUIPMENT INSTALLATION - COMMON REQUIREMENTS

- A.	Install equipment according to approved submittal data.  Portions of the Work are shown only in diagrammatic form.  Refer conflicts to Architect.

- B.	Install equipment level and plumb.

- C.	Install equipment to facilitate service, maintenance, and repair or replacement of equipment components.  Connect equipment for ease of disconnecting, with minimum interference with other installations.  Extend grease fittings to an accessible location.

- D.	Install equipment giving right of way to piping systems installed at required slope.

- 3.03	LABELING AND IDENTIFYING

- A.	Piping Systems: Install pipe markers on each system.  Include arrows showing normal direction of flow.

- 1.	Stenciled Markers: According to ASME A13.1.

- 2.	Plastic markers, with application systems.  Install on insulation segment if required for hot non-insulated piping.

- 3.	Locate pipe markers on exposed piping according to the following:

- a.	Near each valve and control device.

- b.	Near each branch, excluding short takeoffs for equipment and terminal units.  Mark each pipe at branch if flow pattern is not obvious.

- c.	Near locations if pipes pass through walls or floors, or enter inaccessible enclosures.

- d.	At manholes and similar access points that permit view of concealed piping.

- e.	Near major equipment items and other points of origination and termination.

- B.	Equipment:  Install engraved plastic-laminate sign or equipment marker on or near each major item of equipment.

- 1.	Lettering Size: Minimum 1/4-inch- (6.35-mm-) high lettering for name of unit if viewing distance is less than 24 inches (610 mm), 1/2 inch (12.7 mm) high for distances up to 72 inches (1800 mm), and proportionately larger lettering for greater distances.  Provide secondary lettering two-thirds to three-fourths of size of principal lettering.

- 2.	Text of Signs: Provide name of identified unit.  Include text to distinguish between multiple units, inform user of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations.

- C.	Adjusting:  Relocate identifying devices that become visually blocked by work of this or other Divisions.

- 3.04	PAINTING AND FINISHING

- A.	Refer to Division 9 Section "Painting" for paint materials, surface preparation, and application of paint.

- B.	Apply paint to exposed piping according to the following, unless otherwise indicated:

- 1.	Ferrous Piping: Use semi-gloss, acrylic-enamel finish.  Include 2 finish coats over rust inhibitive metal primer.

- 2.	Galvanized-Steel Piping: Use semi-gloss, acrylic-enamel finish.  Include 2 finish coats over galvanized metal primer.

- 3.	Ferrous Supports: Use semi-gloss, acrylic-enamel finish.  Include 2 finish coats over rust-inhibitive metal primer.

- C.	Do not paint piping specialties with factory-applied finish.

- D.	Damage and Touchup: Repair marred and damaged factory-painted finishes with materials and procedures to match original factory finish.

- 3.05	CONCRETE BASES

- A.	Construct concrete bases of dimensions indicated, but not less than 4 inches (150 mm) larger in both directions than supported unit.  Follow supported equipment manufacturer's setting templates for anchor bolt and tie locations.  Use 3000 psig (20.7 MPa), 28-day compressive strength concrete and reinforcement as specified in Division 3 Section, "Cast-in-Place Concrete."

- 3.06	ERECTION OF METAL SUPPORTS AND ANCHORAGE

- A.	Cut, fit, and place miscellaneous metal supports in location, alignment, and elevation to support and anchor utility piping materials and equipment.

- B.	Field Welding: Comply with AWS D1.1, "Structural Welding Code--Steel."

- 3.07	ERECTION OF WOOD SUPPORTS AND ANCHORAGE

- A.	Cut, fit, and place wood grounds, nailers, blocking, and anchorage to support and anchor utility materials and equipment.

- B.	Select fastener sizes that will not penetrate members if opposite side will be exposed to view or will receive finish materials.  Make tight connections between members.  Install fasteners without splitting wood members.

- C.	Attach to substrates as required to support applied loads.

- 3.08	DEMOLITION

- A.	Disconnect, demolish, and remove work specified in Division 2 Sections.

- B.	If pipe, insulation, or equipment to remain is damaged or disturbed, remove damaged portions and install new products of equal capacity and quality.

- C.	Accessible Work: Remove indicated exposed pipe in its entirety.

- D.	Work Abandoned in Place: Cut and remove underground pipe a minimum of 2 inches (50 mm) beyond face of adjacent construction.  Cap and patch surface to match existing finish.

- E.	Removal:  Remove indicated equipment from Project site.

- F.	Temporary Disconnection: Remove, store, clean, reinstall, reconnect, and make operational equipment indicated for relocation.

- 3.09	CUTTING AND PATCHING

- A.	Cut, channel, chase, and drill floors, walls, partitions, ceilings, and other surfaces necessary for utility piping installations.  Perform cutting by skilled mechanics of trades involved.

- B.	Repair cut surfaces to match adjacent surfaces.

- 3.10	GROUTING

- A.	Install nonmetallic, non-shrink grout for equipment-support bearing surfaces, pump and other equipment support plates, and anchors.  Mix grout according to manufacturer's written instructions.

- B.	Clean surfaces that will come into contact with grout.

- C.	Provide forms as required for placement of grout.

- D.	Avoid air entrapment during placing of grout.

- E.	Place grout on concrete bases to provide smooth bearing surface for equipment.

- F.	Place grout around anchors.

- G.	Cure placed grout according to manufacturers’ written instructions.

END OF SECTION 02080