PART I - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02	SUMMARY

RETAIN 1 OF 3 PARAS BELOW.

A.	This Section includes piping and specialties for potable-water service outside the building.

DELETE PARA BELOW IF TAPPING OF UTILITY'S WATER MAIN IS IN THE WORK OF THIS SECTION.  IF RETAINING, EDIT AS REQUIRED.

B.	This Section does not include tapping of utility company water main.

C.	Related Sections include the following:

LIST BELOW ONLY PRODUCTS FOR THIS PROJECT THAT THE READER MIGHT EXPECT TO FIND IN THIS SECTION BUT ARE SPECIFIED ELSEWHERE.  VERIFY THAT SECTION TITLES LISTED BELOW ARE CORRECT FOR THIS PROJECT'S SPECIFICATIONS BECAUSE SECTION TITLES MAY HAVE CHANGED SINCE THIS SECTION WAS UPDATED.

RETAIN SUBPARA ABOVE OR BELOW.

1.	Division 2 Section "Irrigation Work" for irrigation piping.

UTILITIES TYPICALLY PROVIDE WATER METERS, WITH CHARGES BILLED DIRECT, OR THROUGH CONTRACTOR, TO OWNER.  CONTACT UTILITY SERVING THE SITE FOR INFORMATION.  DELETE PARA BELOW IF WATER METERS ARE PROVIDED BY UTILITY OR CONTRACTOR.  IF UTILITY FURNISHES WATER METERS, IDENTIFY UTILITY HERE AND SPECIFY WHAT UTILITY WILL DO; THEN EDIT TEXT AS REQUIRED.

D.	Connection of irrigation system shall be made to existing baseball field’s irrigation man as shown on construction drawings.

1.03	DEFINITIONS

A.	The following are industry abbreviations for plastic and rubber materials:

RETAIN ABBREVIATIONS THAT REMAIN AFTER THIS SECTION HAS BEEN EDITED FOR PROJECT.

1.	NP:  Nylon.

2.	PE:  Polyethylene.

3.	PP:  Polypropylene.

4.	PTFE:  Polytetrafluoroethylene.

5.	PVC:  Polyvinyl chloride.

1.04	SYSTEM PERFORMANCE REQUIREMENTS

A.	Minimum Working Pressures: The following are minimum pressure requirements for piping and specialties, unless otherwise indicated:

EDIT SUBPARAS BELOW AS REQUIRED.

RETAIN SUBPARA ABOVE OR 1 OF 2 SUBPARAS BELOW.

1.	Potable-Water Service: 160 psig.

RETAIN SUBPARA ABOVE OR BELOW IF EXTERIOR FIRE DEPARTMENT CONNECTIONS ARE REQUIRED.

1.05	SUBMITTALS

A.	Product Data: For the following:

DELETE WATER METERS AND WATER-METER BARS BELOW IF PROVIDED BY UTILITY CO.

1.	Water-meter bars.

2.	Backflow preventers.

3.	Pipe and fittings.

4.	Valves.

5.	Yard hydrants.

B.	Shop Drawings: For precast concrete structures.  Include frames and covers and drains.

RETAIN AND EDIT PARA ABOVE OR BELOW AS REQUIRED, OR DELETE BOTH IF DETAILED ON DRAWINGS OR IF NOT REQUIRED.

C.	Shop Drawings: For cast-in-place concrete structures.  Include frames and covers and drains.

DELETE FIRST 2 PARAS BELOW IF NOT REQUIRED.

D.	Record Drawings: At Project closeout of installed water-service piping according to Division 1 Section "Contract Closeout."

E.	Test Reports: As specified in "Field Quality Control" Article in Part 3.

F.	Purging and Disinfecting Reports: As specified in "Cleaning" Article in Part 3.

ELETE WATER METERS BELOW IF PROVIDED BY UTILITY CO.

1.06	QUALITY ASSURANCE

RETAIN PARA BELOW TO ALLOW DRAWING DETAILS BASED ON ONE MFR'S PRODUCT TO ESTABLISH REQUIREMENTS AND STILL ALLOW COMPETITION.  REVISE BELOW TO IDENTIFY SPECIFIC PROPRIETARY SYSTEM OR INDICATE ON DRAWINGS.  CORRELATE WITH DIVISION 1 REQUIREMENTS AND VERIFY THAT SECTION TITLE LISTED IS CORRECT FOR THIS PROJECT'S SPECIFICATIONS.

A.	Product Options: Drawings indicate size, profiles, and dimensional requirements of water-service piping specialties and are based on specific types and models indicated.  Other manufacturers' products with equal performance characteristics may be considered.  Refer to Division 1 Section "Substitutions."

EDIT PARAS BELOW AS REQUIRED OR DELETE IF NOT APPLICABLE.

B.	Comply with standards of authorities having jurisdiction for potable water-service piping.  Include materials, installation, testing, and disinfection.

C.	Comply with NSF 61, "Drinking Water System Components--Health Effects," for materials for potable water.

D.	Comply with ASTM F 645, "Guide for Selection, Design, and Installation of Thermoplastic Water Pressure Piping Systems."

E.	Provide listing/approval stamp, label, or other marking on piping and specialties made to specified standards.

SUBPARA BELOW IS REQUIRED BY SOME FEDERAL AGENCIES.

1.07	DELIVERY, STORAGE, AND HANDLING

- Preparation for Transport:  Prepare valves, including fire hydrants, according to the following:

1.	Ensure that valves are dry and internally protected against rust and corrosion.

2.	Protect valves against damage to threaded ends and flange faces.

3.	Set valves in best position for handling.  Set valves closed to prevent rattling.

B.	During Storage: Use precautions for valves, including fire hydrants, according to the following:

1.	Do not remove end protectors, unless necessary for inspection, then reinstall for storage.

2.	Protect from weather.  Store indoors and maintain temperature higher than ambient dew-point temperature.  Support off the ground or pavement in watertight enclosures when outdoor storage is necessary.

C.	Handling:  Use sling to handle valves and fire hydrants whose size requires handling by crane or lift.  Rig valves to avoid damage to exposed valve parts.  Do not use handwheels or stems as lifting or rigging points.

D.	Deliver piping with factory-applied end-caps.  Maintain end-caps through shipping, storage, and handling to prevent pipe-end damage and to prevent entrance of dirt, debris, and moisture.

E.	Protect stored piping from moisture and dirt.  Elevate above grade.  Do not exceed structural capacity of floor when storing inside.

F.	Protect flanges, fittings, and specialties from moisture and dirt.

G.	Store plastic piping protected from direct sunlight.  Support to prevent sagging and bending.

1.08	PROJECT CONDITIONS

A.	Perform site survey, research public utility records, and verifies existing utility locations.  Contact utility-locating service for area where Project is located.

B.	Verify that water-service piping may be installed to comply with original design and referenced standards.

EDIT OR DELETE BELOW IF SUBSURFACE BORING DATA ARE NOT AVAILABLE.  COORDINATE WITH DIVISION 1 REQUIREMENTS.

C.	Site Information: Reports on subsurface condition investigations made during design of Project are available for informational purposes only; data in reports are not intended as representations or warranties of accuracy or continuity of conditions between soil borings.  Owner assumes no responsibility for interpretations or conclusions drawn from this information.

1.09	SEQUENCING AND SCHEDULING

EDIT PARA BELOW AS REQUIRED IF NEW WATER-SERVICE PIPING WILL CONNECT TO OTHER ON-SITE WATER-SERVICE PIPING.

A.	Coordinate connection to water main with utility company.

B.	Coordinate piping materials, sizes, entry locations, and pressure requirements with building water distribution piping.

C.	Coordinate with other utility work.

PART II - PRODUCTS

2.01	MANUFACTURERS

RETAIN ABOVE FOR NONPROPRIETARY OR BELOW FOR SEMIPROPRIETARY SPECIFICATION.  REFER TO DIVISION 1 SECTION "MATERIALS AND EQUIPMENT."

A.	Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

SEE EDITING INSTRUCTION NO. 1 IN THE EVALUATIONS FOR CAUTIONS ABOUT NAMING PRODUCTS AND MFRS.  DELETE PRODUCT CATEGORIES BELOW IF THEY ARE NOT SPECIFIED OR IF SPECIFIC MFRS ARE NOT REQUIRED.

1.	Drilling-Machine, Sleeves, and Corporation Stops:

a.	Ford Meter Box Co., Inc.

b.	Grinnell Corp, Mueller Company - Water Products Div.

c.	Lee Brass Co.

2.	Bronze Corporation Stops and Valves:

a.	Ford Meter Box Co., Inc.

b.	Grinnell Corp.; Mueller Co.; Water Products Div.

g.	Watts Industries, Inc., James Jones Co.

3.	Tapping Sleeves and Valves:

a.	American Cast Iron Pipe Co.; Waterous Co.

b.	East Jordan Iron Works, Inc.

c.	Grinnell Corp.; Mueller Co.; Water Products Div.

4.	Gate Valves:

b.	American Cast Iron Pipe Co.; American Flow Control Div.

e.	Grinnell Corp.; Grinnell Supply Sales Co.

f.	Grinnell Corp.; Mueller Co.; Water Products Div.

g.	Hammond Valve Corp.

5.	Relief Valves:

a.	Bermad, Inc.

b.	GA Industries, Inc.

c.	MULTIPLEX Manufacturing Co.

6.	Water-Regulating Valves:

a.	Ames Co., Inc.

c.	Cla-Val Co.

g.	Watts Industries, Inc.; Water Products Div.

7.	Backflow Preventers:

a.	Ames Co., Inc.

b.	Cla-Val Co.

f.	Watts Industries, Inc - Water Products Div.

8.	Keyed Couplings:

a.	McWane, Inc., Tyler Pipe, Gustin-Bacon Div.

b.	Victaulic Co. of America.

9.	Protective Enclosures:

a.	Hot Box.

b.	HydroCowl, Inc.

10.	Drains:

b.	Josam Co.

e.	Watts Industries, Inc., Ancon Drain Div.

f.	Zurn Industries, Inc.- Hydromechanics Div.

11.	Sanitary-Type Yard Hydrants:

a.	Murdock, Inc.

12.	Post-Type Yard Hydrants:

a.	Josam Co.

d.	Watts Industries, Inc.- Ancon Drain Div.

f.	Zurn Industries, Inc.- Hydromechanics Div.

2.02	PIPES AND TUBES

SEE EDITING INSTRUCTION NO. 2 IN THE EVALUATIONS FOR SELECTING PIPING MATERIALS.

COORDINATE THIS ARTICLE WITH "PIPE AND TUBE FITTINGS" AND "JOINING MATERIALS" ARTICLES BELOW AND WITH "PIPING APPLICATIONS" ARTICLE IN PART 3.  DELETE PIPE AND TUBE MATERIALS NOT REQUIRED.

A.	General:  Applications of the following pipe and tube materials are indicated in Part 3 "Piping Applications" Article.

SEE "WRITING GUIDE" ARTICLE IN THE EVALUATIONS FOR A DISCUSSION OF THIS SECTION'S ORGANIZATION AND THE MOST EFFICIENT WAY TO EDIT THIS SECTION.

TUBES IN PARA BELOW ARE MADE IN 1/4- TO 12-INCH NPS (DN8 TO DN300).  THESE TUBES ARE USUALLY USED FOR 2-INCH NPS (DN50) AND SMALLER.  2-1/2- TO 3-1/2-INCH NPS (DN65 TO DN90) TUBE IS AVAILABLE BUT USUALLY COSTS MORE THAN 3- OR 4-INCH NPS (DN80 OR DN100) DUCTILE-IRON OR PVC PIPE.

B.	Copper Tube: ASTM B 88, seamless water tube, annealed temper.

PIPES IN 2 PARAS BELOW ARE MADE IN 3- TO 64-INCH NPS (DN80 TO DN1600).  3-INCH NPS (DN80) IS MADE BY ONLY ONE MFR AND MAY NOT BE AVAILABLE.

PIPE IN PARA BELOW IS MADE IN 1/2- TO 6-INCH NPS (DN15 TO DN150).

E.	PE Plastic Pipe: ASTM D 2239, of PE compound and with SIDR required for 160-psig minimum pressure rating.  Include marking "NSF-pw" according to NSF 14.

PIPE IN PARA BELOW IS FM APPROVED IN 3- TO 24-INCH NPS (DN80 TO DN600) FOR CLASS 150 AND IN 4- TO 2-INCH NPS (DN100 TO DN50) FOR CLASS 200.

TUBING IN PARA BELOW IS ONLY MADE IN 1/4- TO 1-INCH NPS (DN8 TO DN25) AT THIS TIME.  THE STANDARD COVERS 1/4- TO 2-INCH NPS (DN8 TO DN50).  VERIFY AVAILABILITY OF 1-1/4- TO 2-INCH NPS (DN32 TO DN50) IF REQUIRED.

PIPE IN PARA BELOW IS MADE IN 1/8- TO 24-INCH NPS (DN6 TO DN600).

F.	PVC Plastic Pipe: ASTM D 1784, Grade 1, Type I, Class 12454-B.

PIPE IN PARA BELOW IS MADE IN 4- TO 12-INCH NPS (DN100 TO DN300).

2.03	PIPE AND TUBE FITTINGS

SEE EDITING INSTRUCTION NO. 2 IN THE EVALUATIONS FOR SELECTING PIPING MATERIALS.

COORDINATE THIS ARTICLE WITH "PIPES AND TUBES" ARTICLE ABOVE, "JOINING MATERIALS" ARTICLE BELOW, AND "PIPING APPLICATIONS" ARTICLE IN PART 3.  DELETE PIPE AND TUBE MATERIALS NOT REQUIRED.  SEE "WRITING GUIDE" ARTICLE IN THE EVALUATIONS.

A.	General:  Applications of the following pipe and tube fitting materials are indicated in Part 3 "Piping Applications" Article.

B.	Copper Fittings: ASME B16.22; wrought-copper, solder-joint pressure type.

C.	Cast-Copper-Alloy Flanges: ASME B16.24, Class 150 or 300, as required for system operating pressure.

D.	Cast-Iron Flanged Fittings: ASME B16.1, Class 125, unless otherwise indicated.

E.	Fittings for PE Plastic Pipe: ASTM D 2609, insert type, made of NP, PP, or PVC plastic; with male, serrated ends matching inside of pipe or threaded ends, as required.  Include corrosion-resistant bands or crimp rings.

F.	PVC Plastic, Socket Fittings: ASTM D 2466, Schedule 40.

FITTINGS IN PARA BELOW ARE ONLY MADE IN 4- TO 8-INCH NPS (DN100 TO DN200).  USE DUCTILE-IRON FITTINGS FOR LARGER SIZES.

G.	PVC Plastic Fittings: UL 1285 and AWWA C907, Class 150.  Include elastomeric seals according to ASTM F 477.

2.04	JOINING MATERIALS

COORDINATE THIS ARTICLE WITH "PIPES AND TUBES" AND "PIPE AND TUBE FITTINGS" ARTICLES ABOVE AND WITH "PIPING APPLICATIONS" ARTICLE IN PART 3.  DELETE JOINING MATERIALS NOT REQUIRED.  SEE "WRITING GUIDE" ARTICLE IN THE EVALUATIONS.

A.	General:  Applications of the following piping joining materials are indicated in Part 3 "Piping Applications" Article.

B.	Refer to Division 2 Section "Utility Materials" for commonly used joining materials.

C.	Ductile-Iron Piping: The following materials apply:

1.	Push-on Joints: AWWA C111 rubber gaskets and lubricant.

2.	Mechanical Joints: AWWA C111 ductile-iron or gray-iron glands, high-strength steel bolts and nuts, and rubber gaskets.

3.	Flanged Joints: AWWA C115 ductile-iron or gray-iron pipe flanges, rubber gaskets, and high-strength steel bolts and nuts.

a.	Gaskets:  Rubber, flat face, 1/8 inch thick, unless otherwise indicated and full-face or ring type, unless otherwise indicated.

b.	Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.

D.	Brazing Filler Metals: AWS A5.8, BCuP Series.

E.	Solder Filler Metal: ASTM B 32, Alloy Sn95, Alloy Sn94, or Alloy E, with 0.10 percent maximum lead content.

F.	Primers for PVC Piping Solvent-Cement Joints: ASTM F 656.

G.	Solvent Cement for PVC Piping Solvent-Cement Joints: ASTM D 2564.

H.	Pipe Couplings: Iron-body sleeve assembly, fabricated to match OD of pipes to be joined.

1.	Sleeve:  ASTM A 126, Class B, gray iron.

2.	Followers:  ASTM A 47, malleable iron; or ASTM A 536, ductile iron.

3.	Gaskets:  Rubber.

4.	Bolts and Nuts: AWWA C111.

5.	Finish:  Enamel paint.

I.	Plastic Pipe-Flange Gasket, Bolts, and Nuts: Type and material recommended by piping system manufacturer, unless otherwise indicated.

2.05	PIPING SPECIALTIES

DELETE PARAS BELOW IF NOT APPLICABLE.

A.	Dielectric Fittings: Assembly or fitting with insulating material isolating joined dissimilar metals to prevent galvanic action and corrosion.

1.	Description:  Combination of copper alloy and ferrous threaded, solder, plain, and weld-neck end types and matching piping system materials.

2.	Dielectric Unions: Factory-fabricated union assembly, designed for 250-psig minimum working pressure at 180 deg F.  Include insulating material isolating dissimilar metals and ends with inside threads according to ASME B1.20.1.

3.	Dielectric Flanges: Factory-fabricated companion-flange assembly, for 150- or 300-psig minimum pressure to suit system pressures.

4.	Dielectric Couplings: Galvanized-steel couplings with inert and non-corrosive thermoplastic lining, with threaded ends and 300-psig minimum working pressure at 225 deg F.

5.	Dielectric Nipples: Electroplated steel nipples with inert and non-corrosive thermoplastic lining, with combination of plain, threaded, or grooved end types and 300-psig working pressure at 225 deg F.

USE THIS ARTICLE FOR BURIED DUCTILE-IRON FITTINGS WITH JOINT SURFACES THAT MIGHT BE DAMAGED BY SOIL AND FOR DUCTILE-IRON PIPING TO BE INSTALLED IN CORROSIVE SOIL.

2.06	VALVES

SEE EDITING INSTRUCTION NO. 2 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING PRODUCTS.

RETAIN ONLY PARAS BELOW FOR VALVE TYPES REQUIRED.

RETAIN UL/FM GATE VALVES FOR USE WITH INDICATOR POSTS AND OS&Y GATE VALVES FOR FIRE-SERVICE PIPING IN PITS IF REQUIRED BY AUTHORITIES HAVING JURISDICTION.

RETAIN 1 OR MORE OF 3 PARAS BELOW FOR UNDERGROUND INSTALLATION FOR USE WITH VALVE BOXES.

A.	Non-rising Stem, Metal-Seated Gate Valves, 3-Inch NPS and Larger: AWWA C500, gray- or ductile-iron body and bonnet; with cast-iron or bronze, double-disc gate, bronze gate rings, bronze stem, and stem nut.  Include 200-psig minimum working-pressure design; interior coating according to AWWA C550; and mechanical-joint ends, unless otherwise indicated.

B.	Non-rising Stem, Resilient-Seated Gate Valves, 3-Inch NPS and Larger: AWWA C509, gray- or ductile-iron body and bonnet; with bronze or gray- or ductile-iron gate, resilient seats, bronze stem, and stem nut.  Include 200-psig minimum working-pressure design, interior coating according to AWWA C550, and push-on- or mechanical-joint ends.

RETAIN VALVES IN PARA BELOW FOR USE WITH INDICATOR POSTS.

VALVES IN 5 PARAS BELOW ARE FOR USE IN PITS.

USE VALVES IN 2 PARAS BELOW WITH SUPERVISORY SWITCHES.

C.	Valve Boxes: Cast-iron box with top section and cover with lettering "WATER," bottom section with base of size to fit over valve and barrel approximately 5 inches in diameter, and adjustable cast-iron extension of length required for depth of bury of valve.

- Provide steel tee-handle operating wrench with each valve box.  Include tee handle with one pointed end, stem of length to operate valve, and socket-fitting valve-operating nut.

USE PARA BELOW FOR UNDERGROUND VALVES.

USE PARA BELOW FOR WALL VALVES.

D.	Curb Stops: Bronze body, ground-key plug or ball, and wide tee head, with inlet and outlet to match service piping material.

E.	Service Boxes for Curb Stops: Cast-iron box with telescoping top section of length required for depth of bury of valve.  Include cover with lettering "WATER," and bottom section with base of size to fit over curb-stop and barrel approximately 3 inches in diameter.

1.	Provide steel tee-handle shutoff rod with each service box.  Include tee handle with one pointed end, stem of length to operate curb stop, and slotted end fitting curb-stop head.

RETAIN ONE OR BOTH PARAS BELOW AS REQUIRED TO CONNECT TO AN EXISTING MAIN UNDER PRESSURE.

RETAIN PARA BELOW FOR CONNECTIONS LARGER THAN 2-INCH NPS (DN50).

RETAIN PARA BELOW FOR CONNECTIONS 2-INCH NPS (DN50) AND SMALLER.

F.	Service Clamps and Corporation Stops: Complete assembly, including service clamp, corporation stop, and bolts and nuts.  Include service clamp and stop compatible with drilling machine.

1.	Service Clamp: Cast iron or ductile iron with gasket and AWWA C800 threaded outlet for corporation stop, and threaded end straps.

2.	Corporation Stops: Bronze body and ground-key plug, with AWWA C800 threaded inlet and outlet matching service-piping material.

USE SUBPARA BELOW IF UTILITY CO. REQUIRES MULTIPLE CONNECTIONS.

3.	Manifold:  Copper with 2 to 4 inlets as required, with ends matching corporation stops and outlet matching service piping.

ADD CRITERIA TO VALVES IN 5 PARAS BELOW IF REQUIRED.

G.	Ball Valves AWWA C507, Class 250.  Include interior coating according to AWWA C550.

H.	Butterfly Valves: UL 1091, with 175-psig working-pressure rating.

SELECT 1 OF 2 PARAS BELOW.

I.	Check Valves UL 312, with swing clapper and 175-psig working-pressure rating.

2.07	SPECIALTY VALVES

VALVES IN 2 PARAS BELOW ARE USUALLY 2-INCH NPS (DN50) OR LARGER.  SMALLER VALVES WOULD USUALLY BE INSTALLED INSIDE BUILDING.

A.	Air-Release Valve AWWA C512, hydromechanical device to automatically release accumulated air.  Include 300-psig working-pressure design.

2.08	WATER-METER BOXES

SELECT 1 OF 2 PARAS BELOW.

A.	Description:  Cast-iron body and cover for disc-type water meter.  Include lettering "WATER METER" in cover; and slotted, open-bottom base section of length to fit over service piping.

DELETE SUBPARA BELOW IF NOT PERMITTED.

1.	Option:  Base section may be cast-iron, PVC plastic, clay or other pipe.

2.09	BACKFLOW PREVENTERS

A.	General:  Manufactured backflow preventers, of size indicated for maximum flow rate and maximum pressure loss indicated.

B.	Working Pressure: 150 psig minimum, unless otherwise indicated.

C.	2-Inch NPS and Smaller: Bronze body with threaded ends.

D.	2-1/2-Inch NPS and Larger: Bronze, cast-iron, steel, or stainless steel body with flanged ends.

E.	Interior Lining: AWWA C550, epoxy coating for backflow preventers with cast-iron or steel body.

F.	Interior Components: Corrosion-resistant materials.

G.	Strainer on inlet if strainer is indicated.

H.	Hose-Connection Vacuum Breakers: ASSE 1011, nickel plated, with non-removable and manual drain features, and ASME B1.20.7, 3/4-11.5NH threads for garden hose on outlet.  Units attached to rough-bronze-finish hose connections may be rough bronze.

SELECT 1 OF 2 PARAS BELOW.

I.	Reduced-Pressure-Principle Backflow Preventer: ASSE 1013, with OS&Y gate valves on inlet and outlet, and strainer on inlet.  Include test cocks and pressure-differential relief valve with ASME A112.1.2 air-gap fitting located between 2 positive-seating check valves for continuous-pressure application.

1.	Pressure Loss:  12 psig maximum through middle third of flow range.

RETAIN PARA ABOVE OR BELOW.

J.	Antisiphon, Pressure-Type Vacuum Breakers: ASSE 1020, with valves, spring-loaded check valve, and spring-loaded floating disc.  Include test cocks and atmospheric vent for continuous-pressure application.

1.	Pressure Loss:  5 psig maximum through middle third of flow range.

2.10	ANCHORAGES

A.	Clamps, Straps, and Washers: ASTM A 506, steel.

B.	Rods:  ASTM A 575, steel.

C.	Rod Couplings: ASTM A 197, malleable iron.

D.	Bolts:  ASTM A 307, steel.

E.	Cast-Iron Washers: ASTM A 126, gray iron.

F.	Concrete Reaction Backing: Portland cement concrete mix, 3000 psig.

1.	Cement:  ASTM C 150, Type I.

2.	Fine Aggregate: ASTM C 33, sand.

3.	Coarse Aggregate: ASTM C 33, crushed gravel.

4.	Water:  Potable.

2.11	IDENTIFICATION

A.	Refer to Division 2 Section "Earthwork" for underground warning tape materials.

RETAIN PARA ABOVE OR BELOW.

B.	Arrange for detectable warning tapes made of solid blue film with metallic core and continuously printed black-letter caption "CAUTION--WATER LINE BURIED BELOW."

RETAIN BELOW IF NONMETALLIC PIPING IS USED.  EDIT CAPTION IF METAL PIPING WITH ELECTRICALLY INSULATED FITTINGS IS USED.

C.	Nonmetallic Piping Label: Engraved, plastic-laminate label at least 1 by 3 inches, with caption "CAUTION--THIS STRUCTURE HAS NONMETALLIC WATER-SERVICE PIPING," for installation on main electrical meter panel.

PART III - EXECUTION

3.01	EARTHWORK

A.	Refer to Division 2 Section "Earthwork" for excavation, trenching, and backfilling.

B.	Refer to Division 2 Section "Hot-Mix Asphalt Paving" for cutting and patching of existing paving.

C.	Refer to Division 2 Section "Portland Cement Concrete Paving" for cutting and patching of paving.

3.02	PIPING APPLICATIONS

PIPING IS ARBITRARILY LIMITED TO 12-INCH NPS (DN300) AND SMALLER.

SEE EDITING INSTRUCTION NO. 2 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING PRODUCTS.

SELECT PIPING APPLICATIONS FROM PARAS AND SUBPARAS BELOW.  COORDINATE WITH MATERIALS SPECIFIED IN PART 2.

A.	General:  Use pipe, fittings, and joining methods for piping systems according to the following applications:

EDIT FIRST 3 PARAS BELOW AS REQUIRED FOR FITTINGS SPECIFIED IN PART 2.

B.	Potable Water-Service Piping: Use the following:

PIPING LISTED BELOW FOR POTABLE-WATER SERVICE MAY NOT BE SUITABLE FOR FIRE-PROTECTION WATER SERVICE.

RETAIN 1 OF 9 SUBPARAS BELOW.

1.	3/4- to 2-Inch NPS: Copper tube, Type K; copper fittings; and soldered joints.

2.	3/4- to 2-Inch NPS: Copper tube, Type K; copper fittings; and brazed joints.

3.	3/4- to 2-Inch NPS: PE plastic pipe; molded PE plastic fittings; and heat-fusion joints.

RETAIN 1 OF 10 SUBPARAS BELOW.

PIPING IN FIRST 2 SUBPARAS BELOW ARE COST SAVING OPTIONS IF USED INSTEAD OF COPPER TUBING.

4.	Option for 2-1/2- to 3-1/2-Inch NPS: 3- or 4-inch NPS; ductile-iron, mechanical-joint pipe; ductile-iron, mechanical-joint fittings; and mechanical joints.

5.	2-1/2- to 3-1/2-Inch NPS: Copper tube, Type K; copper fittings; and brazed joints.

PIPING LISTED BELOW FOR FIRE-PROTECTION WATER SERVICE MAY NOT BE SUITABLE FOR POTABLE-WATER SERVICE.

RETAIN 1 OF 6 SUBPARAS BELOW.

RETAIN 1 OF 6 SUBPARAS BELOW.

RETAIN 1 OF 2 SUBPARAS BELOW.

3.03	VALVE APPLICATIONS

A.	Drawings indicate valve types to be used.  Where specific valve types are not indicated, the following requirements apply:

1.	Underground Valves, 3-Inch NPS and Larger: AWWA, gate valves, non-rising stem, with valve box.

2.	Underground Valves, 4-Inch NPS and Larger: UL/FM, gate valves, non-rising stem, with indicator post.

3.	Pit and Aboveground Installation Valves, 3-Inch NPS and Larger: AWWA, OS&Y gate valves.

4.	Pit and Aboveground Installation Valves, 2-1/2-Inch NPS and Larger: UL/FM, OS&Y gate valves.

5.	Pit and Aboveground Installation Valves, 2-Inch NPS and Smaller: MSS, non-rising stem gate valves.

3.04	PIPING SYSTEMS - COMMON REQUIREMENTS

A.	General Locations and Arrangements: Drawings indicate general location and arrangement of piping systems.  Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated, unless deviations to layout are approved on Coordination Drawings.

B.	Install piping at indicated slope.

C.	Install components with pressure rating equal to or greater than system operating pressure.

D.	Install piping free of sags and bends.

E.	Locate groups of pipes parallel to each other, spaced to permit valve servicing.

F.	Install fittings for changes in direction and branch connections.

G.	Piping Connections: Unless otherwise indicated, make piping connections as specified below:

1.	Install unions, in piping 2-inch NPS and smaller, adjacent to each valve and at final connection to each piece of equipment with 2-inch NPS or smaller threaded pipe connection.

2.	Install flanges, in piping 2-1/2-inch NPS and larger, adjacent to flanged valves and at final connection to each piece of equipment with flanged pipe connection.

3.	Install dielectric fittings to connect piping of dissimilar metals.

3.05	SERVICE ENTRANCE PIPING

REFER TO DIVISION 15 SECTIONS FOR PIPING MATERIALS INSIDE BUILDING.  REVISE THIS ARTICLE AS REQUIRED.

A.	Extend water-service piping and connect to water-supply source and building water piping systems at outside face of building wall in locations and pipe sizes indicated.

1.	Terminate water-service piping at building wall until building water piping systems are installed.  Terminate piping with caps, plugs, or flanges as required for piping material.  Make connections to building water-piping systems when those systems are installed.

B.	Sleeves and mechanical sleeve seals are specified in Division 15 Section "Basic Mechanical Materials and Methods."

RETAIN AND EDIT PARA BELOW FOR PIPING WITH GASKETED JOINTS OR DELETE BELOW IF NOT REQUIRED.

C.	Install underground piping with restrained joints at horizontal and vertical changes in direction.  Use restrained-joint piping, thrust blocks, anchors, tie-rods and clamps, and other supports.

RETAIN AND EDIT BELOW FOR PIPING WITH GASKETED JOINTS.  DELETE IF NOT REQUIRED OR IF PIPING IS ADEQUATELY RESTRAINED INSIDE BUILDING.

3.06	PIPING INSTALLATION

A.	Water-Main Connection: Arrange for tap in water main, of size and in location indicated, from water utility.

RETAIN PARA ABOVE IF TAP IS MADE BY UTILITY CO.  RETAIN PARA BELOW IF TAP IS MADE BY CONTRACTOR.

RETAIN PARA BELOW FOR TAPPING OF PIPE WITH CONNECTION LARGER THAN 2-INCH NPS (DN50).

B.	Make connections larger than 2-inch NPS with tapping machine according to the following:

1.	Install tapping sleeve and tapping valve according to manufacturers written instructions.

2.	Install tapping sleeve on pipe to be tapped.  Position flanged outlet for gate valve.

3.	Install gate valve onto tapping sleeve.  Comply with AWWA C600.  Install valve with stem pointing up and with cast-iron valve box.

4.	Use tapping machine compatible with valve and tapping sleeve; cut hole in main.  Remove tapping machine and connect water-service piping.

RETAIN PARA BELOW FOR TAPPING OF PIPE WITH CONNECTION 2-INCH NPS (DN50) OR SMALLER.

C.	Make connections, 2-inch NPS and smaller, with drilling machine according to the following:

1.	Install service clamps and corporation stops in size, quantity, and arrangement required by utility company standards and according to manufacturer's written instructions.

RETAIN SUBPARA ABOVE OR BELOW.

DELETE SUBPARA BELOW IF NOT REQUIRED.

D.	Install copper tube and fittings according to CDA's "Copper Tube Handbook."

EDIT PARA BELOW FOR REQUIRED MINIMUM DEPTH IF KNOWN.

E.	Bury piping with depth of cover over top at least 36 inches, with top at least 12 inches below level of maximum frost penetration, and according to the following:

1.	Under Driveways: With at least 36 inches cover over top.

2.	In Loose Gravelly Soil and Rock: With at least 12 inches additional cover.

F.	Install piping under streets and other obstructions that cannot be disturbed, by tunneling, jacking, or combination of both.

3.07	ANCHORAGE INSTALLATION

DELETE THIS ARTICLE IF ANCHORAGES ARE NOT REQUIRED.

A.	Install anchorage for tees, plugs and caps, bends, crosses, valves, and hydrant branches.  Include anchorage for the following piping systems:

1.	Gasketed-Joint, Ductile-Iron, Potable-Water Piping: According to AWWA C600.

2.	Gasketed-Joint, PVC Potable-Water Piping: According to AWWA M23.

B.	Apply full coat of asphalt or other acceptable corrosion-retarding material to surfaces of installed ferrous anchorage devices.

3.08	VALVE INSTALLATION

A.	General Application: Use mechanical-joint-end valves for 3-inch NPS and larger underground installation.  Use threaded- and flanged-end valves for installation in pits.  Use non-rising stem UL/FM gate valves for installation with indicator posts.  Use bronze corporation stops and valves, with ends compatible with piping, for 2-inch NPS and smaller installation.

B.	AWWA-Type Gate Valves: Comply with AWWA C600.  Install underground valves with stem pointing up and with cast-iron valve box.

C.	UL/FM-Type Gate Valves: Comply with NFPA 24.  Install underground valves and valves in pits with stem pointing up and with vertical cast-iron indicator post.

D.	Bronze Corporation Stops and Curb Stops: Comply with manufacturer's written instructions.  Install underground curb stops with head pointed up and with cast-iron curb box.

3.09	IDENTIFICATION INSTALLATION

A.	Install continuous plastic underground warning tape during back filling of trench for underground water-service piping.  Locate 6 to 8 inches below finished grade, directly over piping.

DELETE BELOW IF METALLIC WATER-SERVICE PIPING, WITHOUT ELECTRICALLY INSULATED FITTINGS, WILL BE USED.

B.	Attach nonmetallic piping label permanently to main electrical meter panel.

3.10	FIELD QUALITY CONTROL

A.	Piping Tests: Conduct piping tests before joints are covered and after thrust blocks have hardened sufficiently.  Fill pipeline 24 hours before testing and apply test pressure to stabilize system.  Use only potable water.

B.	Hydrostatic Tests: Test at not less than 1-1/2 times working pressure for 2 hours.

1.	Increase pressure in 50-psig increments and inspect each joint between increments.  Hold at test pressure for one hour; decrease to 0 psig.  Slowly increase again to test pressure and hold for one more hour.  Maximum allowable leakage is 2 quarts per hour per 100 joints.  Remake leaking joints with new materials and repeat test until leakage is within above limits.

C.	Prepare reports for testing activities.

3.11	CLEANING

EDIT THIS ARTICLE AS REQUIRED BY AUTHORITIES HAVING JURISDICTION.

A.	Clean and disinfect water distribution piping as follows:

1.	Purge new water distribution piping and parts of existing piping that have been altered, extended, or repaired before use.

RETAIN SUBPARA BELOW IF WATER DISTRIBUTION IS FIRE-PROTECTION WATER PIPING NOT CONNECTED TO POTABLE-WATER SUPPLY.

DELETE SUBPARA ABOVE AND RETAIN 5 SUBPARAS BELOW IF WATER DISTRIBUTION IS CONNECTED TO POTABLE-WATER SUPPLY.

2.	Use purging and disinfecting procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities, use procedure described in AWWA C651 or as described below:

a.	Fill system or part of system with water/chlorine solution containing at least 50 ppm of chlorine; isolate and allow to stand for 24 hours.

b.	Drain system or part of system of previous solution and refill with water/chlorine solution containing at least 200 ppm of chlorine; isolate and allow to stand for 3 hours.

c.	After allowed standing time, flush system with clean, potable water until no chlorine remains in water coming from system.

d.	Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedure if biological examination shows evidence of contamination.

B.	Prepare reports for purging and disinfecting activities.

END OF SECTION 02510