PART I - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02	SUMMARY

A.	This Section includes storm drainage outside the building.

B.	Related Sections include the following:

LIST BELOW ONLY PRODUCTS AND CONSTRUCTION THAT THE READER MIGHT EXPECT TO FIND IN THIS SECTION BUT ARE SPECIFIED ELSEWHERE.

1.	Division 3 Section "Cast-in-Place Concrete" for concrete structures.

1.03	DEFINITIONS

RETAIN ABBREVIATIONS THAT REMAIN AFTER THIS SECTION HAS BEEN EDITED.

A.	ABS:  Acrylonitrile-butadiene-styrene plastic.

B.	EPDM:  Ethylene-propylene-diene-monomer rubber.

C.	PE or HDPE:  Polyethylene plastic, or High Density Polyethylene plastic.

- PVC:  Polyvinyl chloride plastic.

- CMP: Corrugated Metal Pipe

- RCP: Reinforced Concrete Pipe

1.04	PERFORMANCE REQUIREMENTS

A.	Gravity-Flow, Nonpressure-Piping Pressure Ratings:  At least equal to system test pressure.

EDIT PRESSURE BELOW AS REQUIRED.  A LOWER PRESSURE MAY BE ADEQUATE.

1.05	SUBMITTALS

A.	Shop Drawings:  Include plans, elevations, details, and attachments for the following:

1.	Precast concrete manholes and other structures, including frames, covers, and grates.

DELETE SUBPARA BELOW IF STRUCTURES ARE DETAILED ON DRAWINGS.

2.	Cast-in-place concrete manholes and other structures, including frames, covers, and grates.

DELETE PARA BELOW IF NOT REQUIRED.

B.	Design Mix Reports and Calculations:  For each class of cast-in-place concrete.

C.	Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Do not store plastic structures, pipe, and fittings in direct sunlight.

B.	Protect pipe, pipe fittings, and seals from dirt and damage.

C.	Handle precast concrete manholes and other structures according to manufacturer's written rigging instructions.

1.07	PROJECT CONDITIONS

A.	Site Information:  Perform site survey, research public utility records, and verify existing utility locations.

DELETE PARA BELOW IF NO STRUCTURES OR PIPING IS TO BE CLOSED AND ABANDONED.

B.	Locate existing structures and piping to be closed and abandoned.

DELETE PARA BELOW IF NO EXISTING UTILITIES.  COORDINATE WITH REQUIREMENTS SPECIFIED IN DIVISION 1 SECTION "CONSTRUCTION FACILITIES AND TEMPORARY CONTROLS" FOR TEMPORARY UTILITIES.

C.	Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

EDIT SUBPARA BELOW TO SUIT PROJECT.

1.	Notify owner not less than two days in advance of proposed utility interruptions.

2.	Do not proceed with utility interruptions without ownert's written permission.

PART II - PRODUCTS

2.02	PIPING MATERIALS

A.	Refer to Part 3 "Piping Applications" Article for applications of pipe and fitting materials.

2.03	PIPES AND FITTINGS

SEE EDITING INSTRUCTION NO. 2 IN THE EVALUATIONS FOR CAUTIONS ABOUT SELECTING PIPING MATERIALS.

COORDINATE THIS ARTICLE WITH "PIPING APPLICATIONS" ARTICLE IN PART 3.  DELETE MATERIALS NOT USED.

EDIT PIPE STRENGTH CLASSES AND TYPES AS REQUIRED BY CONDITIONS WHERE PIPE IS USED.

SEE "WRITING GUIDE" ARTICLE IN THE EVALUATIONS FOR A DISCUSSION ON THIS SECTION'S ORGANIZATION AND ON THE MOST EFFICIENT WAY TO EDIT THIS SECTION.

PIPING IN PARA BELOW IS AVAILABLE IN SERVICE AND EXTRA-HEAVY CLASSES AND IN NPS 2 TO NPS 15 (DN50 TO DN375).  PIPE ENDS ARE HUB AND SPIGOT.  JOINTS ARE USUALLY MADE WITH RUBBER GASKETS BUT CAN BE MADE WITH OAKUM AND LEAD IF REQUIRED.

A.	Hub-and-Spigot, Cast-Iron Soil Pipe and Fittings:  ASTM A 74, gray iron, for gasketed joints.

1.	Gaskets:  ASTM C 564, rubber, compression type, thickness to match class of pipe.

PIPING IN PARA BELOW IS AVAILABLE IN NPS 1-1/2 TO NPS 10 (DN40 TO DN250).  JOINTS ARE MADE WITH RUBBER SEALING SLEEVES AND STAINLESS-STEEL OR CAST-IRON COUPLINGS.

B.	Hubless Cast-Iron Soil Pipe and Fittings:  CISPI 301 or ASTM A 888, gray iron, for coupling joints.

RETAIN ONE OF THREE SUBPARAS BELOW.  HEAVY-DUTY COUPLINGS MAKE A RIGID INSTALLATION.

1.	Cast-Iron, Heavy-Duty Couplings:  ASTM C 1277, assembly with housing of gray iron complying with ASTM A 48, stainless-steel bolts, and rubber sealing gasket complying with ASTM C 564.

PIPE IN PARA BELOW IS AVAILABLE IN NPS 3 TO NPS 64 (DN80 TO DN1600).  JOINTS ARE GASKET TYPE.

C.	Ductile-Iron Sewer Pipe:  ASTM A 746, for push-on joints.

FITTINGS IN SUBPARA BELOW ARE AVAILABLE IN NPS 3 TO NPS 48 (DN80 TO DN1200).

1.	Standard-Pattern, Ductile-Iron Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

FITTINGS IN SUBPARA BELOW ARE AVAILABLE IN NPS 3 TO NPS 16 (DN80 TO DN400).

2.	Gaskets:  AWWA C111, rubber.

PIPE IN PARA BELOW IS AVAILABLE IN NPS 14 TO NPS 64 (DN350 TO DN1600).  JOINTS ARE GASKET TYPE.

D.	Ductile-Iron Culvert Pipe:  ASTM A 716, for push-on joints.

FITTINGS IN SUBPARA BELOW ARE AVAILABLE IN NPS 3 TO NPS 48 (DN80 TO DN1200).

1.	Standard-Pattern, Ductile-Iron Fittings:  AWWA C110, ductile or gray iron, for push-on joints.

2.	Gaskets:  AWWA C111, rubber.

PIPING IN PARA BELOW IS AVAILABLE IN NPS 2 TO NPS 6 (DN50 TO DN150).  JOINTS ARE GASKET TYPE.  PIPE WITH MECHANICAL COUPLINGS IN NPS 8 TO NPS 12 (DN200 TO DN300) IS AVAILABLE BY SPECIAL ORDER.

COUPLINGS IN SUBPARA BELOW ARE AVAILABLE BY SPECIAL ORDER.

PIPE IN PARA BELOW AND FITTINGS IN SUBPARA BELOW ARE AVAILABLE IN NPS 4 TO NPS 120 (DN100 TO DN3000).  JOINTS ARE BAND TYPE AND ARE NOT WATERTIGHT.

E.	Corrugated-Steel Pipe:  ASTM A 760/A 760M, Type I, made from ASTM A 929/A 929M, zinc-coated steel sheet for banded joints.

1.	Fittings:  Fabricated to types indicated and according to same standards as pipe.

2.	Connecting Bands:  Standard couplings made for corrugated-steel pipe to form soiltight joints.

PIPE IN PARA BELOW AND FITTINGS IN SUBPARA BELOW ARE AVAILABLE IN NPS 4 TO NPS 120 (DN100 TO DN3000).  JOINTS ARE BAND TYPE AND ARE NOT WATERTIGHT.

F.	Corrugated-Aluminum Pipe:  ASTM B 745/B 745M, Type I, made from ASTM B 744/B 744M, aluminum-alloy sheet for banded joints.

1.	Fittings:  Fabricated to types indicated and according to same standards as pipe.

2.	Connecting Bands:  Standard couplings made for corrugated-aluminum pipe to form soiltight joints.

PIPING IN PARA BELOW IS AVAILABLE IN 3 SDR AND IN NPS 3 TO NPS 12 (DN80 TO DN300).  JOINTS ARE SOLVENT-CEMENT AND GASKET TYPES.

TUBING AND FITTINGS IN PARA BELOW ARE AVAILABLE IN NPS 4 TO NPS 10 (DN100 TO DN250).  JOINTS ARE COUPLING TYPE.

JOINTS MADE USING COUPLINGS IN SUBPARA BELOW ARE SILTTIGHT.

PIPING IN PARA BELOW IS AVAILABLE IN NPS 12 TO NPS 36 (DN300 TO DN900).  JOINTS ARE COUPLING TYPE.  THIS PIPE IS ALSO MADE IN NPS 42 AND NPS 48 (DN1050 AND DN1200), BUT THESE SIZES ARE NOT IN AASHTO STANDARD.

G.	Corrugated PE or HDPE Pipe and Fittings:  ASTM F 405, ASTM F 667, AASHTO M 252, and  AASHTO M 294.

JOINTS MADE USING COUPLINGS IN SUBPARA BELOW ARE SOILTIGHT.

1.	Soiltight Couplings: ASTM F 405, ASTM F 667, AASHTO M 252, and AASHTO M 294, corrugated, matching pipe and fittings to form soiltight joints.

JOINTS MADE USING COUPLINGS IN SUBPARA BELOW ARE SILTTIGHT.

PIPE IN PARA BELOW IS AVAILABLE IN NPS 4 TO NPS 12 (DN100 TO DN300).  JOINTS ARE GASKET TYPE.

PIPE IN PARA BELOW IS AVAILABLE IN NPS 4 AND NPS 6 (DN100 AND DN150).  JOINTS ARE SOLVENT-CEMENT TYPE.  STANDARD INCLUDES NPS 2 TO NPS 18 (DN50 TO DN450), BUT AVAILABILITY IN ALL SIZES IS UNCERTAIN.

H.	PVC Sewer Pipe and Fittings:  According to the following:

PIPING IN SUBPARA BELOW IS AVAILABLE IN 4 SDR AND IN NPS 4 TO NPS 15 (DN100 TO DN375).  JOINTS ARE SOLVENT-CEMENT AND GASKET TYPES.

1.	PVC Sewer Pipe and Fittings, NPS 15 and Smaller:  ASTM D 3034, SDR 35, for solvent-cemented or gasketed joints.

a.	Gaskets:  ASTM F 477, elastomeric seals.

PIPING IN SUBPARA BELOW IS AVAILABLE IN TWO THICKNESSES AND IN NPS 18 TO NPS 36 (DN450 TO DN900).  JOINTS ARE GASKET TYPE.

2.	PVC Sewer Pipe and Fittings, NPS 18 and Larger:  ASTM F 679, T-1 wall thickness, bell and spigot for gasketed joints.

a.	Gaskets:  ASTM F 477, elastomeric seals.

PIPE IN PARA BELOW IS AVAILABLE IN NPS 18 TO NPS 48 (DN450 TO DN1200).  JOINTS ARE GASKET TYPE AND ARE SOILTIGHT.

SEE EDITING INSTRUCTION NO. 4 IN THE EVALUATIONS FOR CAUTIONS ABOUT USING CONCRETE PIPE IN FOUR PARAS BELOW.

PIPING IN PARA BELOW IS AVAILABLE IN THREE CLASSES AND IN NPS 4 TO NPS 36 (DN100 TO DN900).  JOINTS ARE GASKET TYPE.

PIPING IN PARA BELOW IS AVAILABLE IN FIVE CLASSES AND THREE THICKNESSES, AND IN NPS 12 TO NPS 144 (DN300 TO DN3600).  JOINTS ARE GASKET TYPE.

I.	Reinforced-Concrete Sewer Pipe and Fittings:  ASTM C 76, Class III, Wall B, for gasketed joints.

1.	Gaskets:  ASTM C 443, rubber.

PIPE IN PARA BELOW IS AVAILABLE IN THREE CLASSES AND IN SIZES EQUIVALENT TO NPS 15 TO NPS 132 (DN375 TO DN3300) ROUND PIPE.  JOINTS ARE BAND TYPE AND SHOULD BE CONSIDERED ONLY SOILTIGHT.

2.04	SPECIAL PIPE COUPLINGS AND FITTINGS

RETAIN COUPLINGS IN PARA BELOW FOR NONPRESSURE JOINTS BETWEEN DIFFERENT PIPE MATERIALS, FOR PIPES HAVING SMALL DIFFERENCE IN OD, AND FOR PIPES OF DIFFERENT SIZES.

A.	Sleeve-Type Pipe Couplings:  ASTM C 1173, rubber or elastomeric sleeve and band assembly fabricated to mate with OD of pipes to be joined, for nonpressure joints.

1.	Sleeve Material for Concrete Pipe:  ASTM C 443, rubber.

2.	Sleeve Material for Cast-Iron Soil Pipe:  ASTM C 564, rubber.

3.	Sleeve Material for Plastic Pipe:  ASTM F 477, elastomeric seal.

4.	Sleeve Material for Dissimilar Pipe:  Compatible with pipe materials being joined.

RETAIN COUPLINGS IN PARA BELOW FOR NONPRESSURE JOINTS BETWEEN PIPES ONE OR TWO SIZES DIFFERENT IN DIAMETER.

B.	Bushing-Type Pipe Couplings:  ASTM C 1173, rubber or elastomeric bushing fabricated to mate with OD of smaller pipe and ID of adjoining larger pipe, for nonpressure joints.

1.	Material for Concrete Pipe:  ASTM C 443, rubber.

2.	Material for Cast-Iron Soil Pipe:  ASTM C 564, rubber.

3.	Material for Plastic Pipe:  ASTM F 477, elastomeric seal.

4.	Material for Dissimilar Pipe:  Compatible with pipe materials being joined.

RETAIN COUPLINGS IN PARA BELOW FOR FORCE-MAIN-PIPING PRESSURE JOINTS.

SPECIAL FITTINGS IN THREE PARAS BELOW ARE FOR BURIED, DUCTILE-IRON PRESSURE PIPE AND OTHER PIPE WITH SAME DIAMETERS.

JOINTS IN PARA BELOW PROVIDE BOTH OFFSET AND EXPANSION.  INDICATE MINIMUM REQUIRED OFFSET AND EXPANSION DATA ON DRAWINGS.

JOINTS BELOW PROVIDE LINEAR EXPANSION ONLY.

C.	Ductile-Iron Expansion Joints:  Three-piece assembly of telescoping sleeve with gaskets and restrained-type, ductile-iron, bell-and-spigot end sections complying with AWWA C110 or AWWA C153.  Include rating for 250-psig minimum working pressure and for expansion indicated.  Include PE film, pipe encasement.

2.05	MANHOLES

A.	Normal-Traffic Precast Concrete Manholes:  ASTM C 478, precast, reinforced concrete, of depth indicated, with provision for rubber gasketed joints.

1.	Diameter:  48 inches minimum, unless otherwise indicated.

2.	Ballast:  Increase thickness of precast concrete sections or add concrete to base section, as required to prevent flotation.

3.	Base Section:  6-inch minimum thickness for floor slab and 4-inch minimum thickness for walls and base riser section, and having separate base slab or base section with integral floor.

4.	Riser Sections:  4-inch minimum thickness, and lengths to provide depth indicated.

5.	Top Section:  Eccentric-cone type, unless concentric-cone or flat-slab-top type is indicated.  Top of cone of size that matches grade rings.

6.	Gaskets:  ASTM C 443, rubber.

7.	Grade Rings:  Include two or three reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch-diameter frame and cover.

8.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast or anchor into base, riser, and top section sidewalls with steps at 12- to 16-inch intervals.  Omit steps for manholes less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

9.	Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

B.	Heavy-Traffic Precast Concrete Manholes:  ASTM C 913; designed according to ASTM C 890 for A-16, heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for rubber gasketed joints.

1.	Ballast:  Increase thickness of one or more precast concrete sections or add concrete to structure, as required to prevent flotation.

2.	Gaskets:  Rubber.

3.	Grade Rings:  Include two or three reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch-diameter frame and cover.

4.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast or anchor into base, riser, and top section sidewalls with steps at 12- to 16-inch intervals.  Omit steps for manholes less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

5.	Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

C.	Cast-in-Place Concrete Manholes:  Construct of reinforced-concrete bottom, walls, and top; designed according to ASTM C 890 for A-16, heavy-traffic, structural loading; of depth, shape, dimensions, and appurtenances indicated.

1.	Ballast:  Increase thickness of concrete, as required to prevent flotation.

DELETE SUBPARA BELOW IF GRADE RINGS ARE NOT REQUIRED, AND EDIT "MANHOLE FRAMES AND COVERS" PARA BELOW IF FRAME WILL BE CAST IN CONCRETE TOP.

2.	Grade Rings:  Include two or three reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch-diameter frame and cover.

3.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast or anchor into sidewalls with steps at 12- to 16-inch intervals.  Omit steps for manholes less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

D.	Manhole Frames and Covers:  ASTM A 536, Grade 60-40-18, ductile-iron castings designed for heavy-duty service.  Include 24-inch ID by 7- to 9-inch riser with 4-inch minimum width flange, and 26-inch-diameter cover.  Include indented top design with lettering "STORM SEWER" cast into cover.

2.06	CATCH BASINS

A.	Normal-Traffic, Precast Concrete Catch Basins:  ASTM C 478, precast, reinforced concrete, of depth indicated, with provision for rubber gasketed joints.

1.	Base Section:  6-inch minimum thickness for floor slab and 4-inch minimum thickness for walls and base riser section, and having separate base slab or base section with integral floor.

2.	Riser Sections:  4-inch minimum thickness, 48-inch diameter, and lengths to provide depth indicated.

3.	Top Section:  Eccentric-cone type, unless concentric-cone or flat-slab-top type is indicated.  Top of cone of size that matches grade rings.

4.	Gaskets:  ASTM C 443, rubber.

5.	Grade Rings:  Include two or three reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch-diameter frame and grate.

6.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast steps or anchor ladder into base, riser, and top section sidewalls at 12- to 16-inch intervals.  Omit steps for catch basins less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

7.	Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

B.	Heavy-Traffic, Precast Concrete Catch Basins:  ASTM C 913, precast, reinforced concrete; designed according to ASTM C 890 for A-16, heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for rubber gasketed joints.

1.	Gaskets:  Rubber.

2.	Grade Rings:  Include two or three reinforced-concrete rings, of 6- to 9-inch total thickness, that match 24-inch-diameter frame and grate.

3.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast steps or anchor ladder into base, riser, and top section sidewalls at 12- to 16-inch intervals.  Omit steps for catch basins less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

4.	Pipe Connectors:  ASTM C 923, resilient, of size required, for each pipe connecting to base section.

C.	Cast-in-Place Concrete, Catch Basins:  Construct of reinforced concrete; designed according to ASTM C 890 for structural loading; of depth, shape, dimensions, and appurtenances indicated.

1.	Bottom, Walls, and Top:  Reinforced concrete.

2.	Channels and Benches:  Concrete.

3.	Steps:  Fiberglass, individual steps or ladder.  Include width that allows worker to place both feet on one step and is designed to prevent lateral slippage off step.  Cast steps or anchor ladder into sidewalls at 12- to 16-inch intervals.  Omit steps for catch basins less than 60 inches deep.

RETAIN SUBPARA ABOVE OR BELOW.

RETAIN PARA BELOW FOR RECTANGULAR STRUCTURES.

D.	Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for heavy-duty service.  Include flat grate with small square or short-slotted drainage openings.

1.	Size:  24 by 24 inches minimum, unless otherwise indicated.

2.	Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

RETAIN PARA AND SUBPARAS ABOVE OR PARA AND SUBPARA BELOW.

RETAIN PARA BELOW FOR ROUND, MANHOLE-TYPE STRUCTURES.

E.	Frames and Grates:  ASTM A 536, Grade 60-40-18, ductile iron designed for heavy-duty service.  Include 24-inch ID by 7- to 9-inch riser with 4-inch minimum width flange, and 26-inch-diameter flat grate with small square or short-slotted drainage openings.

1.	Grate Free Area:  Approximately 50 percent, unless otherwise indicated.

2.07	STORMWATER INLETS

STORMWATER INLETS ARE MADE OF PRECAST CONCRETE, CAST-IN-PLACE CONCRETE, AND BRICK.  SELECT FROM SIX INLET PARAS BELOW.

EDIT THREE PARAS BELOW TO SUIT UTILITY REQUIREMENTS.

A.	Curb Inlets:  Made with vertical curb opening, of materials and dimensions according to utility standards.

B.	Combination Inlets:  Made with vertical curb and horizontal gutter openings, of materials and dimensions according to utility standards.  Include heavy-duty frames and grates.

RETAIN PARA BELOW WITH EITHER OF LAST TWO PARAS ABOVE.

C.	Frames and Grates:  Heavy-duty frames and grates according to utility standards.

RETAIN, EDIT, OR DELETE FOUR PARAS ABOVE OR FOUR PARAS AND ASSOCIATED SUBPARAS BELOW.

EDIT THREE PARAS BELOW AS REQUIRED, AND DETAIL ON DRAWINGS.

RETAIN PARA BELOW WITH EITHER OF LAST TWO PARAS ABOVE.

2.08	CONCRETE

A.	General:  Cast-in-place concrete according to ACI 318, ACI 350R, and the following:

1.	Cement:  ASTM C 150, Type II.

2.	Fine Aggregate:  ASTM C 33, sand.

3.	Coarse Aggregate:  ASTM C 33, crushed gravel.

4.	Water:  Potable.

B.	Portland Cement Design Mix:  4000 psi minimum, with 0.45 maximum water-cementitious ratio.

1.	Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2.	Reinforcement Bars:  ASTM A 615/A 615M, Grade 60, deformed steel.

EDIT PARA AND SUBORDINATE SUBPARAS BELOW TO SUIT PROJECT.  DELETE IF NOT REQUIRED.

C.	Structure Channels and Benches:  Factory or field formed from concrete.  Portland cement design mix, 4000 psi minimum, with 0.45 maximum water-cementitious ratio.

1.	Include channels and benches in manholes.

a.	Channels:  Concrete invert, formed to same width as connected piping, with height of vertical sides to three-fourths of pipe diameter.  Form curved channels with smooth, uniform radius and slope.

RETAIN ONE OF THREE SUBPARAS BELOW.

1)	Invert Slope:  1 percent through manhole.

b.	Benches:  Concrete, sloped to drain into channel.

RETAIN SUBPARA ABOVE OR BELOW.

1)	Slope:  4 percent.

2.	Include channels in catch basins.

a.	Channels:  Concrete invert, formed to same width as connected piping, with height of vertical sides to three-fourths of pipe diameter.  Form curved channels with smooth, uniform radius and slope.

RETAIN ONE OF THREE SUBPARAS BELOW.

1)	Invert Slope:  1 percent through catch basin.

D.	Ballast and Pipe Supports:  Portland cement design mix, 3000 psi minimum, with 0.58 maximum water-cementitious ratio.

1.	Reinforcement Fabric:  ASTM A 185, steel, welded wire fabric, plain.

2.	Reinforcement Bars:  ASTM A 615/A 615M, Grade 60, deformed steel.

PART III - EXECUTION

3.01	EARTHWORK

A.	Excavating, trenching, and backfilling are specified in Division 2 Section "Earthwork."

3.02	PIPING APPLICATIONS

SEE DIVISION 2 SECTION "SANITARY SEWERAGE" FOR OTHER MATERIALS THAT MAY BE USED FOR THIS APPLICATION.

A.	General:  Include watertight, silttight, or soiltight joints, unless watertight or silttight joints are indicated.

B.	Refer to Part 2 of this Section for detailed specifications for pipe and fitting products listed below.  Use pipe, fittings, and joining methods according to applications indicated.

C.	Gravity-Flow Piping:  Use the following:

SELECT FROM SIX SUBPARAS BELOW.

1.	NPS 3:  Hub-and-spigot, Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

2.	NPS 3:  Ductile-iron sewer pipe; standard-pattern, ductile-iron fittings; gaskets; and

SELECT FROM 12 SUBPARAS BELOW.

3.	NPS 4 to NPS 6:  Hub-and-spigot, Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

4.	NPS 4 to NPS 6:  Hubless cast-iron soil pipe and fittings, couplings, and coupled joints.

5.	NPS 4 and NPS 6:  Corrugated-steel pipe and fittings, connecting bands, and banded joints.

6.	NPS 4 and NPS 6:  Corrugated PE drainage tubing and fittings, soiltight couplings, and coupled joints.

7.	NPS 4 and NPS 6:  PVC sewer pipe and fittings, solvent-cemented joints, or gaskets and gasketed joints.

SELECT FROM 13 SUBPARAS BELOW.

8.	NPS 8 to NPS 15:  Ductile-iron sewer pipe; standard-pattern, ductile-iron fittings; gaskets; and gasketed joints in NPS 8 to NPS 12.  Use ductile-iron culvert pipe; standard-pattern, ductile-iron fittings; gaskets; and gasketed joints in NPS 14 to NPS 16.

9.	NPS 8 to NPS 15:  Corrugated-steel pipe and fittings, connecting bands, and banded joints.

10.	NPS 8 to NPS 15:  Corrugated-aluminum pipe and fittings, connecting bands, and banded joints.

11.	NPS 8 to NPS 15:  Corrugated PE drainage tubing and fittings, soiltight couplings, and coupled joints in NPS 8 and NPS 10.  Use corrugated PE pipe and fittings, soiltight couplings, and coupled joints in NPS 12 and NPS 15.

12.	NPS 8 to NPS 15:  PVC sewer pipe and fittings, solvent-cemented joints, or gaskets and gasketed joints.

13.	NPS 8 to NPS 15:  NPS 12 and NPS 15 reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.  Do not use nonreinforced pipe instead of reinforced concrete pipe in NPS 8 and NPS 10.

SELECT FROM 12 SUBPARAS BELOW.

14.	NPS 18 to NPS 36:  Corrugated-steel pipe and fittings, connecting bands, and banded joints.

15.	NPS 18 to NPS 36:  Corrugated-aluminum pipe and fittings, connecting bands, and banded joints.

16.	NPS 18 to NPS 36:  Corrugated PE pipe and fittings; corrugated, soiltight couplings; and coupled joints.

17.	NPS 18 to NPS 36:  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

SELECT FROM NINE SUBPARAS BELOW.

18.	NPS 42 to NPS 120:  Corrugated-steel pipe and fittings, connecting bands, and banded joints.

19.	NPS 42 to NPS 120:  Corrugated-aluminum pipe and fittings; connecting bands; and banded joints.

20.	NPS 42 and NPS 48:  Similar pattern to corrugated PE pipe and fittings; corrugated, soiltight couplings; and coupled joints.

21.	NPS 42 to NPS 144:  Reinforced-concrete sewer pipe and fittings, gaskets, and gasketed joints.

3.03	SPECIAL PIPE COUPLING AND FITTING APPLICATIONS

A.	Special Pipe Couplings:  Use where required to join piping and no other appropriate method is specified.  Do not use instead of specified joining methods.

1.	Use the following pipe couplings for nonpressure applications:

a.	Sleeve type to join piping, of same size, or with small difference in OD.

b.	Increaser/reducer-pattern, sleeve type to join piping of different sizes.

c.	Bushing type to join piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

2.	Use pressure-type pipe couplings for force-main joints.  Include PE film, pipe encasement.

B.	Special Pipe Fittings:  Use where indicated.  Include PE film, pipe encasement.

3.04	INSTALLATION, GENERAL

SEE EDITING INSTRUCTION NO. 3 IN THE EVALUATIONS FOR CAUTIONS ABOUT INSTALLING PIPE MATERIALS.

A.	General Locations and Arrangements:  Drawing plans and details indicate general location and arrangement of underground storm drainage piping.  Location and arrangement of piping layout take design considerations into account.  Install piping as indicated, to extent practical.

B.	Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.  Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.  Maintain swab or drag in line, and pull past each joint as it is completed.

C.	Use manholes for changes in direction, unless fittings are indicated.  Use fittings for branch connections, unless direct tap into existing sewer is indicated.

D.	Use proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

E.	Install gravity-flow piping and connect to building's storm drains, of sizes and in locations indicated.  Terminate piping as indicated.

EDIT TWO SUBPARAS BELOW TO SUIT PROJECT.

1.	Install piping pitched down in direction of flow, at minimum slope of 1 percent, unless otherwise indicated.

F.	Extend storm drainage piping and connect to building's storm drains, of sizes and in locations indicated.  Terminate piping as indicated.

3.05	PIPE JOINT CONSTRUCTION AND INSTALLATION

A.	General:  Join and install pipe and fittings according to installations indicated.

B.	Refer to Division 2 Section "Utility Materials" for basic piping joint construction and installation.

C.	Hub-and-Spigot, Cast-Iron Soil Pipe and Fittings:  With rubber gaskets according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook."  Use gaskets that match class of pipe and fittings.

DELETE SUBPARA BELOW IF NOT REQUIRED.

RETAIN ONE OF TWO PARAS BELOW THAT MATCHES SELECTION IN "PIPES AND FITTINGS" AND "PIPING APPLICATIONS" ARTICLES ABOVE.

D.	Hubless Cast-Iron Soil Pipe and Fittings:  With CISPI-type couplings according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

DELETE SUBPARA BELOW IF NOT REQUIRED.

E.	Hubless Cast-Iron Soil Pipe and Fittings:  With heavy-duty-type couplings according to CISPI 310, CISPI's "Cast Iron Soil Pipe and Fittings Handbook," and coupling manufacturer's written instructions.

DELETE SUBPARA BELOW IF NOT REQUIRED.

F.	Ductile-Iron Sewer Pipe with Ductile-Iron Fittings:  According to AWWA C600.

DELETE SUBPARA BELOW IF NOT REQUIRED.

G.	Install with top surfaces of components, except piping, flush with finished surface.

RETAIN ONE OF TWO PARAS BELOW THAT MATCHES SELECTION IN "PIPES AND FITTINGS" AND "PIPING APPLICATIONS" ARTICLES ABOVE.

H.	Corrugated-Steel Pipe:  Join and install according to ASTM A 798.  Use standard joints made with coupling bands, unless otherwise indicated.

I.	Corrugated-Steel Pipe:  Join and install according to ASTM A 798.  Use soiltight joints made with coupling bands and gaskets, unless otherwise indicated.

RETAIN ONE OF TWO PARAS BELOW THAT MATCHES SELECTION IN "PIPES AND FITTINGS" AND "PIPING APPLICATIONS" ARTICLES ABOVE.

J.	PE Pipe and Fittings:  As follows:

1.	Join pipe, tubing, and fittings with couplings for soiltight joints according to manufacturer's written instructions.

2.	Install according to ASTM D 2321 and manufacturer's written instructions.

3.	Install corrugated piping according to the Corrugated Polyethylene Pipe Association's "Recommended Installation Practices for Corrugated Polyethylene Pipe and Fittings."

K.	PVC Pressure Pipe and Fittings:  Join and install according to AWWA M23.

L.	PVC Sewer Pipe and Fittings:  As follows:

1.	Join pipe and gasketed fittings with gaskets according to ASTM D 2321.

2.	Install according to ASTM D 2321.

M.	Concrete Pipe and Fittings:  Install according to ACPA's "Concrete Pipe Installation Manual."  Use the following seals:

1.	Round Pipe and Fittings:  ASTM C 443, rubber gaskets.

N.	System Piping Joints:  Make joints using system manufacturer's couplings, unless otherwise indicated.

O.	Join piping made of different materials or dimensions with couplings made for this application.  Use couplings that are compatible with and that fit both systems' materials and dimensions.

3.06	MANHOLE INSTALLATION

A.	General:  Install manholes, complete with appurtenances and accessories indicated.

DELETE PARA BELOW IF NOT REQUIRED.

B.	Set tops of frames and covers flush with finished surface of manholes that occur in pavements.  Set tops 3 inches above finished surface elsewhere, unless otherwise indicated.

C.	Install precast concrete manhole sections with gaskets according to ASTM C 891.

D.	Construct cast-in-place manholes as indicated.

E.	Install fiberglass manholes according to manufacturer's written instructions.

3.07	CATCH-BASIN INSTALLATION

A.	Construct catch basins to sizes and shapes indicated.

B.	Set frames and grates to elevations indicated.

3.08	STORM DRAINAGE INLET AND OUTLET INSTALLATION

A.	Construct inlet head walls, aprons, and sides of reinforced concrete, as indicated.

B.	Construct riprap of broken stone, as indicated.

C.	Install outlets that spill onto grade, anchored with concrete, where indicated.

D.	Install outlets that spill onto grade, with flared end sections that match pipe, where indicated.

E.	Construct energy dissipators at outlets, as indicated.

3.09	CONCRETE PLACEMENT

A.	Place cast-in-place concrete according to ACI 318 and ACI 350R.

3.10	DRAINAGE SYSTEM INSTALLATION

A.	Assemble and install components according to manufacturer's written instructions.

B.	Install with top surfaces of components, except piping, flush with finished surface.

C.	Assemble channel sections to form slope down toward drain outlets.  Use sealants, adhesives, fasteners, and other materials recommended by system manufacturer.

D.	Embed channel sections and drainage specialties in 4-inch minimum concrete around bottom and sides.

E.	Fasten grates to channel sections if indicated.

F.	Embed trench sections and drainage specialties in 4-inch minimum concrete around bottom and sides.

3.11	CLEANOUT INSTALLATION

A.	Install cleanouts and riser extension from sewer pipe to cleanout at grade.  Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts and cast-iron soil pipe for riser extensions to cleanouts.  Install piping so cleanouts open in direction of flow in sewer pipe.

B.	Set cleanout frames and covers in earth in cast-in-place concrete block, 18 by 18 by 12 inches deep.  Set with tops 1 inch above surrounding earth grade.

C.	Set cleanout frames and covers in concrete pavement with tops flush with pavement surface.

3.12	DRAIN INSTALLATION

A.	Install type of drains in locations indicated.

B.	Fasten grates to drains if indicated.

C.	Set drain frames and covers with tops flush with pavement surface.

3.13	CLOSING ABANDONED STORM DRAINAGE SYSTEMS

EDIT THIS ARTICLE TO SUIT PROJECT.

A.	Abandoned Piping:  Close open ends of abandoned underground piping indicated to remain in place.  Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed.  Use either procedure below:

- Close open ends of piping with at least 8-inch-thick, brick masonry bulkheads.

B.	Abandoned Structures:  Excavate around structure as required and use one procedure below:

1.	Remove structure and close open ends of remaining piping.

2.	Backfill to grade according to Division 2 Section "Earthwork."

3.14	FIELD QUALITY CONTROL

A.	Clear interior of piping and structures of dirt and superfluous material as work progresses.  Maintain swab or drag in piping, and pull past each joint as it is completed.

1.	In large, accessible piping, brushes and brooms may be used for cleaning.

2.	Place plug in end of incomplete piping at end of day and when work stops.

3.	Flush piping between manholes and other structures to remove collected debris, if required by authorities having jurisdiction.

B.	Inspect interior of piping to determine whether line displacement or other damage has occurred.  Inspect after approximately 24 inches of backfill is in place, and again at completion of Project.

1.	Submit separate reports for each system inspection.

2.	Defects requiring correction include the following:

a.	Alignment:  Less than full diameter of inside of pipe is visible between structures.

b.	Deflection:  Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 92.5 percent of piping diameter.

c.	Crushed, broken, cracked, or otherwise damaged piping.

d.	Infiltration:  Water leakage into piping.

e.	Exfiltration:  Water leakage from or around piping.

3.	Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

4.	Reinspect and repeat procedure until results are satisfactory.

C.	Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

1.	Do not enclose, cover, or put into service before inspection and approval.

2.	Test completed piping systems according to authorities having jurisdiction.

3.	Leaks and loss in test pressure constitute defects that must be repaired.

4.	Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

END OF SECTION 02630