PART I - GENERAL

  - SCOPE

- This section covers all items fabricated from metal shapes, plates, rods and bars except component parts of equipment and items covered by other sections.

- Fabricated metal items, which are detailed on the drawings but not mentioned specifically herein, shall be fabricated in accordance with the applicable requirements of this section.

  - RELATED WORK SPECIFIED ELSEWHERE

- Steel Joists - Section 05200

- Metal Decking - Section 05300

  - REFERENCED STANDARDS FOR QUALITY ASSURANCE

- All work shall be in accordance with the applicable sections, and references therein, of the Specifications and Standards of the following:

- Manual of Steel Construction by American Institute of Steel Construction (AISC).

- American Society of Testing Materials (ASTM)

- American Welding Society (AWS)

- Steel Structures Painting Council (SSPC)

- Welded Steel Tube Institute (WSTI)

- In conflicts between this specification, industry standards and/or local building codes, the more stringent requirements shall govern.

  - SUBMITTALS

- Shop drawings in accordance with project procedures showing all dimensions, locations, connection details, notes, accessories, and other materials related to the furnishing, fabricating, testing, painting and erection of the structural steel required by these specifications.

- Shop drawings shall show complete bolting and welding information, both shop and field, using appropriate symbols.

- Shop drawings shall be not be made by reproduction of design drawings.  Steel erection drawings and detail sheets prepared by steel fabricator shall all be of the same size sheets and approximately the size of the design drawings.

- Shop drawings shall be reviewed for conformance to specific project requirements by the contractor before being submitted to the Engineer for approval.

PART II - PRODUCTS

  - MAIN, SECONDARY MEMBERS & BASE PLATES

- Rolled Sections - ASTM A-992, Fy=50 ksi.

- Steel Pipe - ASTM A-501, Fy=36 ksi.

- Tube Sections - ASTM A-500, Grade "B", Fy=46 ksi or Grade "C", Fy=50 ksi.

  - BOLTS

- Bolted shop and field connections shall be made with high strength, friction type nuts and washers conforming to ASTM A-325 or A-490.  Bolts shall have an identifying mark of three (3) radial lines.

- Non-friction bolt connections may be with bolts conforming to ASTM A-307.

- All bolts shall be 3/4" diameter unless otherwise shown on drawings.

  - WELDING ELECTRODES

- All welding electrodes shall be E-70 series.

  - PAINT

- Unless otherwise noted shop coat paint may be fabricator's standard but shall be compatible with final field painting.  Touch-up paint used in the field shall be the same type paint used for the shop coat and shall be delivered to the job in sealed containers clearly marked with manufacturer's name and brand.

- Finish paint shall be as specified elsewhere in this specification.

- Lintels shall receive two coats of shop paint before placing.

  - GROUT

- Grout for base plates shall be a ready-to-use, non-metallic, non-corrosive product requiring only addition of water at job site to produce a flowable grouting material having no drying shrinkage at any age.  Compressive strength of grout shall be not less than 5000 psi at 28 days.

PART III - EXECUTION

  - FABRICATION

- Fabricate from approved shop drawings using members cut from full-length stock.  Members may be spliced only where shown.

- Members shall be free from twist, bends, buckles or open joints.

- Shop connections may be bolted or welded.  Welds, bolt size, number and spacing shall be determined by the AISC Standards.  Fabricator shall design and be responsible for all connections.  Connections for beams which cannot conform to the typical connection details shall be in accordance with the following:

- Where beam reactions are not shown on the drawings connection details shall be detailed for the end reaction resulting from the maximum uniform load which the beam will support (as simple beam) for the span on the drawing.

- Where beam reactions are shown on the drawings, the connections shall develop the reactions shown.

- Where connections are subject to eccentricity, such eccentricity shall be taken into account when detailing the connections.

- Bearing surfaces shall be planed to true beds.  Abutting surfaces shall be closely fitted.  Tubular sections shall be completely seal-welded at all joints, seams, and splices.

- Structural steel shall be provided with all holes for attaching wood, masonry, furring, sash angle clips and other parts.

- Fascia beams and other steel requiring accurate alignment shall be provided with slotted holes and/or washers for aligning the steel accurately.  No erection bolts or other fastening parts or joints or rolled stamping names shall show on finished surfaces of exposed steel, exterior or interior.

- Lintels shall have 8" minimum bearing each side of opening.

- Shop connections may be welded except as noted.  Field connections shall be welded or made with the high strength steel bolts except for girts, stair stringers and handrails which may be field bolted with machine bolts.  All welding shall be done by operators qualified by AWS Standards.  Certificate shall be furnished when requested. Welding techniques, appearance and quality shall conform to AWS Standards.  Continuous jet welding may be employed at all exposed connections requiring a smooth weld in lieu of conventional welds that require grinding.

  - SHOP PAINT

- All steel shall be shop cleaned per SSPC-SP3 and primer paint applied immediately thereafter.  Except for steel to be field welded, surfaces shall be covered evenly and thoroughly and worked into joints.  Paint shall be applied to dry surfaces.  Parts inaccessible after assembly shall be given two (2) coats of the specified shop paint.

- Shop primer shall have a minimum dry film thickness of 1.2 mils.

- Contact surfaces shall be cleaned before assembly but shall not be painted.  Machine finished surfaces shall be protected against corrosion by a suitable coating.

  - STORAGE OF MATERIAL

- Site storage of all structural steel shall be as directed by the job superintendent.

- All steel shall be stored on blocking so that no metal touches the ground and will be protected against bending under its own weight and water will not collect thereon.

  - ERECTION

- Steel shall be erected level and plumb within AISC tolerances.  No final bolting or welding shall be done until structure is properly aligned.  The structure shall be secured against all dead load, wind and erection stresses.  Temporary bracing shall be used where necessary and shall remain in place as long as required for safety.

- Bolting shall be done with high strength friction type bolts and hardened washers.  Set high strength bolts by the turn-of-the-nut method as specified by the "Research Council On Riveted and Bolted Structural Joints".

- Holes for turned bolts to be inserted in the field shall be reamed in the field.  Erection bolts are not to be used on exposed surfaces.  Erection bolts or other surfaces and stiffeners shall not interfere with architectural clearances.

- No additional holes or cutting of steel work other than shown on the Drawings shall be done without the written permission and approval of the Owner's representative.

- Light drifting necessary to draw the holes together will be permitted, but drifting to match unfair holes will not be allowed.  Twist drills shall be used to enlarge holes as necessary to make connections.  Reaming that weakens the members or makes it impossible to fill the holes properly or to adjust accurately after reaming will not be allowed.  Enlarging holes by burning is prohibited.

- Welding - See Paragraph 3.01 H - Protect all adjacent finished surfaces during the progress of welding.  Damaged surfaces shall be replaced at cost of the erection contractor.

  - FIELD PAINTING (TOUCH-UP)

- After the structural steel has been erected and before any superimposed construction is placed, apply one field coat of paint to all places where the shop coat of paint has rubbed away; where the shop coat of paint was omitted because of field welding, or where field welding has damaged the shop coat of paint.  Apply field paint to the structural steel and bar joists before roof deck is applied.

- Touch-Up Paint - After erection is completed, all field bolts, field welds, abrasions, etc. shall be cleaned and spot painted.  Paint shall be same material used for the shop coat and shall be applied evenly with no runs, etc.

  - FIELD QUALITY CONTROL

- The steel contractor shall secure the services of a testing laboratory as approved and accepted by the local authorities and the owner/engineer to provide qualified inspectors for the following inspections.

- All shop and field connections

- Qualifications of welders

- Daily calibration of impact wrenches used for high strength bolting

- Visual inspection of all work after erection

- Testing agency shall interpret tests and state in each report whether test specimens comply with requirements and specifically state any deviations therefrom.

- Costs of all inspections shall be paid for by the steel contractor.  Testing laboratory shall send reports of all inspections directly to the engineer and owner and elsewhere as directed.

- Bolted connections shall be tested for minimum fastener tension for bolt size and grade specified in conformance with the AISC.  Inspection for tightness shall be the arbitration method thus:

- Ten percent (10%) of all bolted connections, but not less than two (2) bolts (selected at random) in each connection shall be tested.  Test shall be made with an "inspecting wrench" adjusted to "job inspection torque".  If no nut or bolt head is turned, the connection shall be accepted.  If any nut or bolt head is turned, all bolts and nuts in the entire connection shall be tested.  Contractor shall tighten all bolts in any connection in which a test bolt failed and resubmit the connection for re-inspection.  All costs for re-tightening of bolts shall be borne by this Contractor.

- Welded connections may be inspected visually unless otherwise noted on contract drawings.  However if any weld appears inadequate the engineer can require magnetic particle or ultrasonic testing without any additional cost to owner.

  - CLEAN-UP

After the completion of this work, remove from the site all excess materials and debris.  Leave entire work in a neat and orderly condition ready for inspection.

END OF SECTION