PART I - GENERAL

1.01	WORK DESCRIPTION

A.	Provide all labor, materials, and equipment required to complete installation as specified herein and shown on plans.

PART II - PRODUCTS

  - ELECTRICAL EQUIPMENT

- Motor controllers, starters, protective devices, etc. for control and protection of equipment shall be furnished with the equipment.  Installed by Mechanical Contractor and electrically connected to power source under "Electrical Division".

- Provide both overload and under voltage protection in all phases.  Where interlock or automatic operation is specified, regardless of HP, provide magnetic starter complete with "run-off-auto" switch so connected that in "run", all safety controls can stop the motor.

- Size two and larger starters shall have control circuits individually fused from line side of starter.

- Motors ½ HP and smaller, 120 volts, single phase, (unless noted otherwise).  Motors ¾ HP and larger, 3 phase voltage as noted.  Motors shall be rated for continuous, full-load duty and be capable of withstanding momentary overloads of 50 percent.

- Provide dual element fuses for all hermetic motors above ¾ HP.

- NEMA Standards shall be taken as minimum requirements for electrical equipment.

- Contactors shall be UL. listed for 100,000 cycles of operation.

- Where starters are in outdoor conditions, contractor to furnish NEMA 3R enclosure with ambient compensating heaters.

PART III - EXECUTION

  - ELECTRICAL WORK

- All electrical power wiring shall be done under Division 16.  All control devices, starters, wiring, contactors, etc.  shall be provided and installed by Division 15.

- Control wiring shall be by Mechanical Contractor.  All electrical work shall comply with requirements set forth in Division 16.  Minimum control wiring sizes shall be #12 AWG for 120 volts or higher, and #18 AWG for low voltage wiring which shall both be run in conduit.

- The Contractor shall verify the available electrical characteristics before ordering equipment.

  - EXCAVATION AND BACKFILL

- This Contractor shall do all necessary excavation required for installation of his work.  Each utility shall have its own trench.

- Excavation for piping shall be cut a minimum of 6" below the required grade and a 6" bed of sand or unclassified gravel back-filled to serve as the bedding for the pipe.

- Where trenches are over 5'-0" in depth, sides shall be shored up to prevent cave-in during construction.  Remove all timber before starting to backfill.

- After work has been tested and approved, the Contractor shall backfill all trenches.  Backfill shall consist of a layer of washed gravel to 12" above the pipe, and dirt fill, free from rocks, debris, and cinders.  Where ductile iron pipe is shown or specified, backfill shall be dirt only as described above.

- Install backfill material in 12" layers.  Compact to 95% standard proctor.  If more stringent, compact backfill to a dry density equal to that required by Contract for the location.

  - CUTTING AND PATCHING

- The General Contractor shall provide new openings in new construction required by this Division.  This Contractor is responsible for location and size of openings required by his work.  This Contractor is solely responsible for providing all pipe sleeves, sealing of openings, and all openings required for his work in existing construction.

- All other cutting, patching, and drilling for the installation of this work shall be provided under this Division.

- Structural members shall not be cut without prior approval of the Architect.

- Patching shall be of quality equal to, and in appearance, matching existing construction, and shall be performed under the Section of the specifications covering these materials.

  - FLASHING

- All piping passing through roof shall be flashed with a flashing fitting approved by the roofing manufacturer.   Flashing shall be of size to match pipe served.

- Offset pipe under roof so no roof penetration is closer than 48" to roof edge.

- Make roof drains watertight with 4 lbs. per square foot sheet lead extending at least 12" from drain rim into membrane waterproofing and clamped to drain.

  - MINIMUM REQUIREMENTS

- Code requirements are minimum and shall be complied with at no additional cost.  Where requirements of these drawings and specifications exceed code requirements, work shall be furnished and installed in accordance with drawings and specifications. Any work done contrary to the requirements shall be removed and replaced without incurring additions to the contract.

  - FREEZE PROTECTION

- Inspect all drawings carefully for locations subject to freezing conditions.  Do not install piping in exterior walls, ventilated attic or ceiling spaces, or other locations where freezing may occur unless otherwise noted in the plans.

- Piping systems throughout the building shall be protected from freezing, generally by installing pipes on the heated side of building insulation.  Piping adjacent to exterior walls shall be installed in furred spaces with building insulation between the piping and the exterior wall.

END OF SECTION