PART I - GENERAL

  - Where the word "piping" is used, it shall mean pipes, fittings, nipples, valves, and all other accessories as required for continuous and complete systems of piping.

  - Use latest edition of "Standards" or "Federal Specifications".

# PART II - PRODUCTS

  - Black steel pipe shall conform to ASTM A120.  Fittings for pipe up to 2½" shall be screwed type.  Fittings for pipe 3" and over shall be welding type fittings. Fittings shall meet the following:

- Malleable Iron:	ASA - B-16-3

- Cast Iron:	ASA - B-16-4

- Welding Type:	ASA - B-16-9

  - Galvanized steel pipe shall be ASTM A120 hot-dipped per ASTM A120.  Fittings as above, except hot-dipped galvanized drainage type.

  - Copper pipe and fittings shall conform to ASTM B88 specifications for hard drawn pipe and ASTM B-280 for soft annealed copper tubing.  Tubing shall be marked for type identification.  Fittings shall be wrought, solder sweat type. For potable water systems joints shall be sweat soldered using 95-5 solder with water-soluble flux approved for potable water systems.  Use 95-5 solder with “Nokorode” flux for all other applications.

  - Bell and spigot cast iron soil pipe and fittings shall comply with ASTM Standard A-74 and shall be coated inside and outside.  Joints shall be made with positive seal elastomeric compression type gaskets.

  - No-Hub cast iron pipe and fittings shall comply with the Cast Iron Soil Pipe Institute Standard 301-69-T and shall be coated inside and outside.  Joints shall be made with neoprene gaskets meeting ASTM C-564 and stainless steel couplings.

  - PVC-DWV piping for use outside and within building shall meet ASTM-D-2665.  Joints shall be made with solvent cement meeting ASTM 2564.  Pipe, fittings, and solvent cement shall carry the NSF seal of approval.

  - Ductile iron, pipe and fittings shall conform to ANSI/AWWA C150/A21.50 with "Tyton" joints for straight lengths, mechanical joints at fittings, and restraint devices where rodded.

  - SLEEVES

- Floor, non-bearing walls - 22 gauge galvanized steel.

- Bearing walls above ground - galvanized steel pipe.

- Foundations, underground walls - extra heavy cast iron pipe.

- See detail for vented underground gas piping.

  - ESCUTCHEONS

- Exposed in finished areas: chrome plated with SETSCREW.

- Exposed in unfinished areas: Steel plates anchored to wall or cast brass with SETSCREW.

  - VALVES shall be as follows (or equal):

- Gate:  Milwaukee 1149

- Globe: Milwaukee 1502

- Check: Milwaukee 1509

- Angle: Milwaukee  504

- Ball:  Watts B5901

- Hose Bibbs: Chicago #293 with vacuum breaker, ¾” size.

- Non Freeze Hydrants: Josam-Box #71000, Wall #71050.  Indoor Hydrant.  Josam #71020.

- Gas Cock:  DeZurik #425 with RS49 seal and #483 lever.

- Butterfly: Centerline # AO12105-01

- Triple Duty: Amtrol #TD

- Diverting: Centerline series A  8" C.I. tee w/#30300 double acting, bello-frame type 80 positioner 3-15# (pneumatic).

- PRV: Wilkins 500C sizes 1/2" to 2", Wilkins 500FC sizes above 2".

- Reduced pressure backflow preventor: Wilkins 975SLX-AG.

PART III - EXECUTION

  - Arrange and install piping approximately as indicated, straight and plumb, and as directed as possible, forming right angles or parallel lines with building walls.

  - Locate groups of pipes parallel to each other, spacing them a distance to permit applying full insulation and to permit access to service valves.

  - All piping shall be installed to allow for movement due to expansion and contraction.

  - Do not locate water lines above electrical equipment.

  - Where changes in pipe size occur, use only reducing fittings.  Where dissimilar piping joins, use dielectric fittings.

  - Ream pipe out, turn on end, and wipe clean before installing cut piping.

  - Screwed joints shall be made tight, metal to metal, using "Teflon" tape.

  - No exposed piping used about plumbing fixtures shall show tool marks or more than two threads at fittings.

  - Sleeves shall be two sizes larger than pipe when uncovered and one pipe size larger than overall outside diameter of pipe and insulation when covered.  All penetrations through masonry walls shall be core drilled and sleeved. Sleeves are required where a pipe passes through a wall or floor. Pipes passing through a wall or floor must be individually sleeved unless approved by Architect.

- Sleeves shall finish flush with the finished wall and ¼-inch above the finished floor

(NO SHARP EDGES).

  - Provide escutcheons wherever exposed pipes, hanger rods, etc. pass through floors, walls, and ceilings. Escutcheons shall fit OD. of insulation.

  - Piping specified for use within building shall extend a minimum of 5'-0" beyond building walls, unless otherwise noted.

  - On black steel gas piping exposed to weather, areas with damaged coating and welded or screwed joints to be wire brushed free of rust, primed with “Rustoleum” oxide primer and sprayed with 2 (two) finish coats of black enamel.

  - Rough-in locations shall be in accordance with manufacturer's instructions except where piping or escutcheon will interfere with items such as bases around walls.  Piping interfering with bases will be removed and relocated.

  - All piping in finished areas of building shall be concealed except where otherwise noted on the drawings.

  - VALVES

- All valves shall be installed so that they are easily accessible for operation and maintenance.  Where valves are indicated in any concealed area, offset close to surface of material and install a metal, locking access door of adequate size to service valve.  Engineer shall approve exact location prior to installation.

- Valves shall be installed with stems vertical.

- Where valves are located outside building, provide a reinforced concrete valve box with cover or a three-piece cast iron valve box.  All covers shall be secured to body with vandal-proof screw.

- Use ball valves for all domestic water lines 2" and below, and gate valves for 2 ½” and larger.

## END OF SECTION