PART I - GENERAL

  - Entire insulation system, including insulation, jackets, finishes, adhesives, shall be U.L. listed as non-combustible.  Flame spread rating shall be less than 25, fuel contributed less than 50 and smoke generated less than 50.

  - Provide a complete and CONTINUOUS installation of insulation from equipment, device or fixture to main service entrance or point of discharge.

## PART II - PRODUCTS

  - PIPING

- Owens-Corning "One-Piece" fiberglass pipe insulation with FRJ jacket with self-sealing lap.

  - Domestic cold water: 1/2” thick.

  - Domestic hot water and hot water recirculating piping above grade: 1" thick.

- Vapor barrier adhesive: Foster 30-35.

- All exposed piping in mechanical rooms and shall be covered with hard white PVC jacket, 0.20" thick solvent welded as manufactured by Zeston or equal.

  - DUCTWORK

- Internal Acoustical Liner: Certain-Teed "Ultralite" heavy graduated density, 1" thick.

- External Duct Insulation:  Certain-Teed Duct Wrap Insulation, 2" thick, with Type LV facing for all other systems

- All liner to meet ASTM G21 and G22 for micro-biological treatment.

  - HANDICAP FIXTURES- Provide Zurn Z-8996-2 stop/supply and trap protector.

PART III - EXECUTION

  - PIPE

- Insulation shall have all sides and end joints butted together tightly.  Adhere SSL by pressurizing it with a hard tool.  Provide 3" butt strips at each end of joint and seal in same manner as longitudinal joints.

- All fittings and valves shall be insulated with pre-molded fittings insulation.  Coat each fitting with two 1/8" coats of vapor barrier mastic, reinforced with glass fabric extending 2" onto adjacent pipes.

  - DUCTWORK

- All rectangular supply, outside and return air ductwork shall have internal acoustical liner.  Diffuser necks shall be externally insulated.

- Boots and boxes for grilles and registers above grade to be externally wrapped, below grade, lined internally.

- Acoustical liner shall be cemented to the ductwork by a solid coat of bonding adhesive spread over entire surface. Liner shall be secured with Foster's "Clip-Fas" hangers (one per square foot) in addition to the adhesive.

- All round pipe to be wrapped with external insulation and sealed with manufacturer’s tape for vapor proof installation.  External insulation shall be wrapped tightly on the ductwork with all circumferential joints butted and longitudinal joints overlapped a minimum of 2".  Adhere with 4" strips of bonding adhesive at 8" on center, 2" flange in circumferential joint and overlap in longitudinal joints shall be stapled with flare-door staples on 6" centers and taped with 3" wide full reinforced Kraft tape.

- Contractor shall provide and install a weatherproof insulation system on all ductwork exposed to outside weather conditions. The system will utilize a 1 ½” thick polystyrene or polyisocyanurate closed cell rigid board insulation with a vapor barrier system equal to Polyguard Products, Inc. Alumaguard 60. All materials will be installed as per the manufacturer’s specifications.

- The contractor shall provide and install fiberglass insulation with vapor barrier for all ductwork exposed to outside temperature conditions (i.e. attic, crawl space, etc…). The duct system shall be externally wrapped with all longitudinal joints overlapping a minimum of 2”. All other joints to be butted and sealed. All materials will be installed as per the manufacturer’s specifications.

# END OF SECTION