1.01	GENERAL

- Contractor shall furnish all labor, materials, equipment and incidentals required to provide two explosion-proof submersible centrifugal sewage grinder pump(s) for NEC class 1, division 1, group C, D hazardous locations and fiberglass reinforced polyester tank (TRST System).  Duplex units, containing two grinder pump and all necessary parts and equipment, shall be installed in fiberglass reinforced polyester tanks for outside installation. All equipment shall be factory installed, except for externally mounted control panel, gravity sewer inlet hubs and pump assembly, which are to be installed in the field.

- The contractor shall supply a control panel which contains all necessary components for proper starting and operation of the pumps including start capacitor, start relay, and run capacitors for single Ø pumps.  This panel shall provide a circuit that monitors the seal sensors, heat sensors in the pump.

- Pump shall be equipped with stainless steel nameplate.  An optional name plate stating the unit is accepted for use in NEC Class 1, division 1, group C, D, hazardous locations with third party, (Factory Mutual,) approval.

- Each pre-assembled duplex station shall include the basin, basin cover, complete grinder pump, quick disconnect rail system, check valve, junction box, start-stop level controls, motor high temperature shut-off, motor seal leak alarm, high water alarm, all internal wiring terminating into the junction box, shutoff valve, and schedule 80 discharge piping.  In addition, an external alarm and pump control panel is to be provided for each unit.

- The stations shall be by the same manufacturer as supplying the pump and control panel so as to insure suitability and assurance of experience in matching the equipment required for a complete grinder pumping     station together, and to insure single source responsibility for the complete package.  All residential stations shall be U.L. listed as an assembly by the manufacturer.  The manufacturer shall have a minimum of five (5) years experience in the manufacture and supply of residential grinder stations and shall have a minimum of five thousand (5,000) units installed.

2.01	OPERATING CONDITIONS

- Each pump shall be rated 2 H.P., 230 volts, 1 phase, 60 hertz, 3450 R.P.M. The unit shall produce 13 G. P. M. at 97 ft TDH.

3.01	CONSTRUCTION

- The pump shall be a centrifugal, submersible, grinder, wastewater type, model G1X as manufactured by Hydromatic Pumps.  The pump volute, motor and seal housing shall be high quality gray cast iron, ASTM A-48, Class 30.  The pump discharge shall be fitted with a 1¼" NPT flange.  All external-mating parts shall be machined and Buna N Rubber O-ring sealed on a beveled edge.  Gaskets shall not be acceptable. All fasteners exposed to the pumped liquids shall be 300 series stainless steel.

- The controls for the pump shall be contained in a non-corrosive fiberglass enclosure meeting NEMA 4X requirements with a hinged door and neoprene gasket.

- The enclosure shall have provisions for padlocking. A nameplate shall be permanently affixed to the panel and include the model number, voltage, phase, hertz, ampere rating and horsepower rating. A warning label against electric shock shall be permanently affixed to the outer door

- A steel back panel with electroplated bright zinc and clear chromate finish shall be provided. A painted steel back panel will not be acceptable.

- Run lights and hand-off-auto switches shall be provided. Run light and hand-off-auto switch shall be mounted on an electroplated bright zinc with clear chromate finish steel bracket. The run light and hand-off-auto switch shall be properly labeled as to function. The hand-off-auto switch shall be rocker type with an electrical life of 50,000 operations. The run light shall match the hand-off-auto switch in appearance and have an electrical life of 5,000 hours. Run light shall be red.

- The incoming power shall be  230  volts,  1  phase, 60 hertz service. Terminal blocks with box type lugs shall be supplied to terminate all wiring for floats and heat and seal sensors for the pump, if required. The pump leads shall be terminated at the overload relay or at box type terminal blocks. The terminal blocks for the float connections shall be on the pump controller.

- A circuit breaker shall be used to protect from line faults and to disconnect the pump from the incoming power. Circuit breaker shall be thermal magnetic and sized to meet NEC requirements for motor controls.

- The magnetic starters shall include a contactor with a minimum mechanical life of 3,000,000 operations and a minimum contact life of 1,000,000 operations. A definite purpose contactor shall not be acceptable. The magnetic starter shall include an overload relay which is ambient temperature compensated and bimetallic. The overload relay shall have test and reset buttons. The overload relay shall be capable of being set in either manual or automatic reset mode. In the manual mode, reset shall be accomplished only by the operator. At 6 times full load amps the overload relay shall trip within 10 seconds or Class 10 rated overload relays shall be required.

- Control voltage shall be 120 VAC and may be accomplished by the means of a transformer or available line voltage. A control fuse and on/off switch shall protect and isolate the control voltage from the line.

- Wire ties shall be used to maintain panel wiring in neat bundles for maintenance and to prevent interference with operating devices. All wiring shall be color coded to facilitate maintenance and repair of the control panel. Where a color is repeated, number coding shall be added. A schematic shall be permanently attached to the inside surface of the front door.

- All ground connections shall be made with ring tongue terminals and star washers to assure proper ground.

- Pump controller shall have provisions for connecting float level controls and heat sensor monitors, where applicable, to box type lug connectors.

- Box type lug connectors shall be made of polyamide thermoplastic to exclude aging due to heat influences. Phenolic type terminal blocks on the pump controller shall not be acceptable. Each terminal block shall be property and permanently labeled on the pump controller as to its purpose

3.02	ELECTRICAL POWER CORD

- Electrical power cord shall be STW-A, water resistant 600 V, 60°C., UL and CSA listed and applied dependent on amp draw for size.

- The power cable entry into the cord cap assembly shall first be made with a compression fitting. Each individual lead shall be stripped down to bare wire at staggered intervals, and each strand shall be individually separated.  This area of the cord cap shall then be filled with an epoxy compound potting which will prevent water contamination to gain entry even in the event of wicking or capillary attraction.

- The power cord leads shall then be connected to the motor leads with extra heavy connectors having brass inserts with a screwed wire to wire connection, rather than a terminal board that allows for possible leaks.

- The cord cap assembly where bolted to the connection box assembly and the connection box assembly where bolted to the motor housing shall each be sealed with a Buna N Rubber O-ring on a beveled edge to assure proper sealing.

3.03	MOTOR

- The stator, rotor and bearings shall be mounted in a sealed submersible type housing.  The stator windings shall have Class F insulation, (155°C or 311°F), and a dielectric oil filled motor, NEMA B design (3 Ø) NEMA L design (1 Ø).  Further protection shall be provided by on winding thermal sensors.  Because air-filled motors do not dissipate heat as efficiently as oil-filled motors, they shall not be acceptable.

- The pump and motor shall be specifically designed so that they may be operated completely submerged in the liquid being pumped.  The pump shall not require cooling water jackets.  Dependence upon, or use of, water jackets for supplemental cooling shall not be acceptable.

- Stators shall be securely held in place with a removable end ring and threaded fasteners so they may be easily removed in the field without the use of heat or a press.  Stators held by a heat shrink fit shall not be acceptable.  Stators must be capable of being repaired or rewound by local motor service station.  Units that require service only by the factory shall not be acceptable.  No special tools shall be required for pump and motor disassembly.

- Pump shall be equipped with heat sensors.  The heat sensor(s) (one on single phase, two on three phase) shall be a low resistance; bi-metal disc that is temperature sensitive.  It shall be mounted directly on the stator windings and sized to open at 120°C and automatically reset at 30-35°C differential.  The sensors shall be connected in series with motor starter coil so that the pump cease operation when an over-temperature condition is sensed.  The starter shall be equipped with 3-leg overload relay with heaters sized for the pump’s full load amps.  The pump shall cease operation when the overload is tripped.  The overload shall be manually reset.

3.04	BEARINGS AND SHAFT

- An upper radial bearing and a lower thrust bearing shall be required.  These shall be permanently lubricated by the dielectric oil that fills the motor housing.

- The shaft shall be machined from a solid 416 stainless steel bar and is a design that is of large diameter with minimum overhang to reduce shaft deflection and prolong bearing life.

3.05	SEALS

- The pump shall have two mechanical seals, mounted in tandem, with an oil chamber between the seals. The upper seal shall be a John Crane Type 21, BF1C1; seals shall be used with the rotating seal faces being carbon and the stationary seal faces to be ceramic.  The lower seal shall be a John Crane Type 6A BP892.  The seal shall be replaceable without disassembly of the seal chamber and without the use of special tools.  Pump-out vanes shall be present on the backside of the impeller to keep contaminates out of the seal area.  Units that require the use of foreign manufactured seals shall not be acceptable. Seals shall be locally available.

- The pump shall be equipped with a seal leak detection probe and warning system.  This shall be designed to alert maintenance personnel of lower seal failure without having to take the unit out of service for inspection or requiring access for checking seal chamber oil level and consistency.

- There shall be an electric probe or seal failure sensor installed in the seal chamber between the two tandem mechanical seals.  If the lower seal fails, contaminants which enter the seal chamber shall be detected by the sensor and send a signal to operate the specified warning device.

- Units equipped with opposed mechanical seals shall not be acceptable.

3.06	IMPELLER

- Impeller shall be bronze multi-vane, semi-open non-overloading design and have pump-out vanes on the backside of the impeller to prevent grit and other materials from collecting in the seal area.  The impeller shall be designed so that it can factory or field trimmed to meet specific performance conditions.  Wear or field trimming shall not deter the factory balance.

- Impellers shall be dynamically balanced. The tolerance values shall be listed below according to the International Standard Organization grade 6.3 for rotors in rigid frames.

RPM	Tolerance

3500	.01 in. - oz./lb. of impeller weight

3.07	CASING

- The casing shall be of the end suction volute type having sufficient strength and thickness to withstand all stress and strain from service at full operating pressure and load.  The casing shall be of the vertical discharge type.  A rail system to allow easy installation and removal of the pump shall be available.  The design shall be such that the pumps will be automatically connected to the discharge piping when lowered into position with the guide rails.  The casing shall be accurately machined and bored for register fits with the suction and casing covers.

  - GRINDER CUTTERS

- The combination centrifugal impeller and grinder unit shall be attached to the common motor and pump shaft made of 416 stainless steel.  The grinder unit shall be on the suction side of the pump impeller and discharge directly into the impeller inlet leaving no exposed shaft to permit packing of ground solids.  The grinder shall consist of two stages.  The cutting action of the second stage shall be perpendicular to the plane of the first cut for better control of the particle size.  The grinder shall be capable of grinding all materials found in normal domestic sewage, including plastics, rubber, sanitary napkins, disposable diapers, and wooden articles into a finely ground slurry with a particle dimension no greater than ¼ inch.  Both stationary and rotation cutters shall be made of 440C stainless steel hardened to Rockwell 60 C and ground to close tolerance.

- The upper (axial) cutter and stationary cutter ring shall be reversible to provide new cutting edges to double life.  The stationary cutter ring shall be a slip fit into the suction opening of the volute and held in place by three (3) 300 series stainless steel screws and retaining ring.  The lower (radial) cutter shall macerate the solids against the I. D. of the cutter ring and extrude them through the slots of the cutter ring.  The upper (axial) cutter shall cut off the extrusions, as they emerge from the slots of the cutter ring to eliminate any roping effect, which may occur in single stage cutting action.  The upper (axial) cutter shall fit over the hub of the impeller and the lower (radial) cutter shall slip fit and be secured by means of peg and hole and rotate simultaneously with the rotation of the shaft and impeller.  A 300 series stainless steel countersunk washer in conjunction shall lock the grinding mechanism to the shaft with a 300 series stainless steel flat head cap screw threaded into the end of the shaft.

3.09	PAINTING

- The pump shall be painted after assembly, and testing, with a dark green water reducible air dry enamel.  The paint shall be applied in one coat covering all exterior surfaces.  The pump shall be air dried after testing and before painting.

3.10	SERVICEABILITY

- The complete rotating assembly shall be capable of being removed from the volute without disturbing discharge piping or volute.  The motor housing, seal housing with seal plate and impeller still attached to the shaft shall be capable of being lifted out of the volute case from the top as one assembly.

3.11  	BASIN

A.	The basin shall be  36" diameter with a depth (8’) as shown on the plans.  The basin shall be molded of fiberglass reinforced polyester resin manufactured by the filament wound technique to assure that the interior surface is smooth and resin rich.  The basin shall have a minimum wall thickness of 1/4 inch.  An anti-floatation ring base shall be molded as an integral part of the basin assembly and shall be a minimum of 3" in diameter.

3.12  	BASIN COVER

A.	The cover shall be of reinforced fiber filled to withstand 350 PSF live load rating.  The cover shall be bolted to the basin with stainless steel cap screws.  Stainless nuts shall be embedded in the fiberglass to prevent turning.

3.13  	GUIDE RAIL / PIPING MODULE

A.	Guide rail shall be mounted in the basin on a stainless steel riser support which is to be securely mounted to the basin side wall.  Guide rail shall be PVC corrosion resistant channel that when mounted to the PVC corrosion resistant discharge elbow will allow the pump, using the self cleaning ball check valve, to be lifted in and out of the station without any of the discharge piping being disturbed.  Discharge piping shall be 1-1/4" schedule 80 PVC.  Shut off valve shall be 1-1/4" PVC schedule 80 with shut off extension handle that is operational   without personnel entering the wetwell.

3.14 	CHECK VALVE

A.	Check valve shall be 1-1/4" schedule 80 PVC threaded on one end with a hydraulic flange on the other end.  Check valve shall be self cleaning with a neoprene rubber ball and shall allow the pump to be removed from the station without making any disconnects.

3.15  	JUNCTION BOX

A.	A U.L. nema 6 junction box shall be provided.  The junction box shall be formed from corrosion resistant, flame retardant thermoplastic.  Junction box shall have a hinged cover for ease of service.  Float switches shall be   suspended from a stainless steel holder securely mounted to the basin wall.

3.16	CONTROL PANEL

A.	Hydromatic model SPC control panel shall be supplied, compatible with package equipment specified herein.

B.	The motor control panel shall be assembled and tested by a shop meeting U.L. standard 508 for industrial      controls.  The motor and control panel shall be assembled and tested by the same manufacturer supplying the pump so as to insure suitability and assurance of experience in matching controls to motors and to insure single source responsibility for the equipment

4.01	TESTING

- Commercial testing shall be required and include the following:

- The pump shall be visually inspected to confirm that it is built in accordance with the specification as to HP, voltage, phase and hertz.

- The stator motor leads shall be tested for integrity using a megohmeter at the highest setting.

- Pump shall be allowed to run dry to check for proper rotation.

- Discharge piping shall be attached; the pump submerged in water and amp readings shall be taken in each leg to check for an imbalanced stator winding.  If there is a significant difference in readings, the stator windings shall be checked with a bridge to determine if an unbalanced resistance exists.  If so, the stator shall be replaced.

- The pump shall be removed from the water, megohmeter tested again, dried and the motor housing filled with dielectric oil.

- In addition to the above commercial testing, a special megohmeter test shall be performed and include the following:

- The pump shall be submerged in water and allowed to run at maximum load for 30 minutes.

- A written report on the above shall be prepared by the test engineer, certified and submitted to the engineer.

- (OPTIONAL) A hydrostatic test shall also be performed on the pump.  The hydrostatic test shall require that the volute and impeller be removed and a fixture installed to hold the spring and lower mechanical seal in place.  A double plate, gasket and through bolt shall be installed on the pump.  A discharge mating flange, gasket and pressure fitting shall be installed.  The inlet port, volute and discharge nozzle shall then be pressurized with water to 150% of the maximum pump shut off pressure.  This hydrostatic pressure shall be maintained for at least 5 minutes and the housing checked for leaks and/or loss of pressure.

5.01	WARRANTY

A.  	The pump unit or any part thereof shall be warranted against defects in material or workmanship within one year from date of installation or 18 months from date of manufacture, whichever comes first, and shall be replaced at no charge with a new or manufactured part, F.O.B. factory or authorized warranty service station.  The warranty shall not assume responsibility for removal, reinstallation or freight, nor shall it assume responsibility of incidental damages resulting from the failure of the pump to perform.  The warranty shall not apply to damage resulting from accident, alteration, design, misuse or abuse.

END OF SECTION