PART I - GENERAL

  - SCOPE OF WORK

- Work under this Section includes all domestic cold and hot water systems inside the building to a point outside building as shown.

- Any and all charges by Utility Company shall be paid by this Contractor.

## PART II - PRODUCTS

  - Water lines shall be:

- Type "K" soft drawn copper - underground.

- Type "L" hard drawn copper - above ground.

  - Water heater relief lines to be Type "L", hard drawn copper pipe and fittings, supported as water lines. Discharge to be full size of relief valve.

  - Reduced pressure backflow preventer:  Wilkins 975XLS-AG full line size.

## PART III - EXECUTION

  - Outdoor piping shall be at least 3'-0" below grade.

  - Test piping hydrostatically at 125 psi before applying insulation, for thirty minutes without drop in pressure.  Notify authorities before test is to take place.  Provide certificate of inspection.

  - Grade all piping towards main water service entrance to building and provide drain valves where grading of branches becomes impossible to drain to main water service, provide accessible, concealed hose thread drain valve.

  - Provide air chambers min. 12” – max 18” high and one pipe diameter larger than supply pipe in cold and hot water to fixture when not otherwise protected by shock absorbers.

  - Provide pressure reducing stations per detail on drawings.

  - No underground piping shall be covered prior to inspection by Engineer.

  - Piping joints shall be cleaned after soldering.  Flux shall be low corrosion type. Joints which have solder or flux drippings on pipe will be remade or replaced at discretion of Engineer. No lead bearing solder permitted.

  - Where local utility company requires backflow preventer on water service, locate adjacent to PRV station, and provide vent drain of adequate size to hub drain or service sink.

  - STERILIZATION

- Flush system until water flows clear from all openings. Disinfect using a mixture of water and calcium hypochlorite in such proportions as to produce a chlorine dose of 50 PPM after 24 hours.

- Hold treated water in system for at least 24 hours during which time all valves, pumps, tanks and fixtures shall be operated at least five minutes or five times.

- Upon completion, flush entire system until chlorine content is less than 10 PPM.

- Do Not Proceed with sterilization of indoor water piping until quality of water in outdoor distribution system has been accepted.

# END OF SECTION