PART I - GENERAL

  - CONNECTIONS TO EQUIPMENT

- This Contractor shall make all connections to equipment furnished under this section of the specifications.

- Each fixture and piece of equipment shall be connected into piping systems using unions, or union fittings and service valves on both "in" and "out" connections.  Connections to fixtures shall be concealed where possible.  Flanged connections do not require unions.

- All equipment shall be installed in strict conformance with manufacturer’s recommendations, as specified herein and as shown.

- All welders shall be qualified by an independent testing agency and certified in accordance with the requirements of ASME Section IX of the Boiler and Pressure Vessel Code.  Contractor shall furnish certification of welders qualifications with shop drawings.

  - ADJUSTING AND BALANCING

- It shall be the responsibility of this Contractor to completely adjust and balance the system to provide performance desired.  He shall furnish the Owner with clean copies of all instrument readings and quantities leaving and entering units, in main trunks, outside air intakes and reliefs, exhaust fan main branches and each inlet, delivery from supply registers, and return registers, fan motor running amperage and rated full load amps, etc.  Air quantities shall be balanced to within 5% of those shown on drawings.

### PART II - PRODUCTS

  - RECORD DOCUMENTS

- The Contractor shall furnish the Owner with one complete set of reproducible drawings and two complete, clean sets of specifications showing installed locations, size, etc., of all work and material as taken from record documents.

- Provide three sets of 1.) Manufacturer's operating and maintenance instructions for each piece of equipment and 2.) Terminal-to-terminal automatic control diagram showing all wiring and interlocks.  Bind this information into 8½" x 11" booklets.

### PART III - EXECUTION

  - CLEANING

- This Contractor shall clean all equipment and accessories free from rust, grease, plaster, etc. before being placed in operation.

- Units being run during the construction process shall be provided with clean filters.  Filters shall be checked and changed during this time.  Upon final acceptance change filters.

  - PAINTING

- This Contractor shall paint all piping, equipment, supports, and other ferrous metal which is not otherwise protected against corrosion.  When factory paint has been damaged, it shall be touched-up to give an appearance similar to adjacent surface. Clean thoroughly all surfaces before painting.

- Rusted work shall be wire brushed free of rust and primed with rust inhibitive primer as directed.

  - MARKING

- This Contractor shall label all relays, valves, thermostats, equipment, switches, etc.  Labeling of equipment other than valves shall be done with engraved plastic signs showing white letters on red background.  Valves shall be labeled with valve tags.  Tag numbers shall correspond to a valve listing which shall list function, area or equipment served and normal position.  This listing shall be mounted under glass as directed.

- Piping shall be marked 20 feet on center for straight runs in open areas and 10 feet on center in mechanical rooms and closed areas.  Vertical lines shall be labeled minimum one per floor.  Pipe identification shall be "Seaton Name Plate Corporation", "Setmark" or equal in appearance by contractor with the following designations:

## PIPE				COLOR

  - Water		GB

  - Domestic Hot Water	Y

Note:  Y = Yellow with Black Letters; GB = Green with Black Letters

  - OPERATION TEST AND INSTRUCTIONS

- Give all equipment furnished under this Contract an operational test prior to final acceptance.  Notify Engineer 48 hours in advance of these tests.  Failure to notify the Engineer will require these tests be repeated if directed.

- This Contractor shall instruct Owner's representative on the proper care, operation, and control of system if necessary for up to two eight-hour days.

# END OF SECTION