PART I - GENERAL

  - All materials and equipment shall be properly supported and hung to keep piping, ductwork, and equipment to an even grade throughout its installation.  All hangers and supports shall be of ample size to safely support the load imposed and shall be provided complete.

  - Fasten supports to building in the following order of preference:

- Steel Framing

- Concrete

- Wood Framing

- Masonry

- Wood Sheathing

  - Adhesives are not acceptable as mounting or supporting devices.

  - All hangers or upper attachments, which are to be supported by structural members, shall attach to the upper chord and at the panel point.  In no case shall any load be imposed to bracing, bridging, angle or other portion of the member.

## PART II - PRODUCTS

  - PIPE

- Steel, Cast Iron, or PVC pipe        	Fee & Mason #103

- Copper Pipe (Horizontal)             	Fee & Mason #500

- Copper Pipe (Vertical)

  - DUCTWORK

- Horizontal - straps in accordance with SMACNA.  Wire will not be allowed.

- Vertical - over 8'-0" angle support from adjacent surface screwed to duct.

PART III - EXECUTION

  - Hanger and support spacing for horizontal pipes shall be as follows:

- Cast Iron Pipe: 5'-0" or every other joint, whichever is closer.

- Steel Pipe: 7'-0" for pipe 1-½" and smaller and 10'-0" for all other.

- Copper Pipe: 6'-0" for pipe 1-½" and smaller and 10'-0" for all other.

- PVC Pipe: 4'-0" or every other joint, whichever is closer, and at each change in direction.

  - Support hanger from wood using coach screws on open construction and hanger flanges on sheeting, from concrete using inserts, from steel using beam clamps, rivets, or bolts, and from concrete block using toggle bolts or through bolts.

  - Hangers and supports shall be placed at each offset or change of direction of piping, at end of branches and at risers.  Any pipe riser exceeding 8 feet shall have riser clamps 6 feet on center.

  - Where supports are required by in-line pumps, plumbing fixtures or other pieces of equipment, contractor to furnish supports compatible and intended for equipment.

  - The Contractor shall provide all equipment supports and upper structural materials required by equipment which he furnishes that is to be suspended from framing members, bracketed on walls, or supported clear of floor and roof.

  - Provide pipe clamps behind each supply line to fixtures, on outside of insulation, to prevent movement in any direction.  Flush valves, stops, etc. which have movement will be corrected by installing clamps behind wall. Escutcheons shall not be considered a clamping device.

  - "Unistrut" support system and pipe clamp to be of adequate size for placement of ½" "Armaflex" or equal at point of clamp.  Install Armaflex at each clamp, extending ½" each side with neat appearance.

  - Pipe hangers for suspending horizontal insulated piping shall be sized to fit around the pipe, pipe insulation and pipe insulation shield (if any).

# END OF SECTION