PART I - GENERAL

  - Furnish and install a complete UL listed system of heaters, components, and controls to prevent pipelines from freezing.

  - All water piping shown on plans exposed to ambient temperatures shall be electrically traced to point of termination to equipment or conditioned space.

### PART II - PRODUCTS

  - The self-regulating heater shall consist of two (2) 16 AWG tinned-copper bus wires embedded in parallel in a self-regulating polymer core that varies its power output to respond to temperature all along its length, allowing the heater to be crossed over itself without over-heating, to be used directly on plastic pipe and to be cut to length in the field.  The heater shall be covered by a radiation cross-linked modified polyolefin dielectric jacket.

  - In order to provide energy conservation and to prevent overheating, the heater shall have a self-regulating factor of at least 90 percent.  The self-regulation factor is defined as the percentage reduction, without thermostatic control, of the heater output going from 40 degree F pipe temperature operation to 150 degree F pipe temperature operation.

  - The heater shall operate on line voltages of 120 volts without the use of transformers.

  - The heater be sized according to the following table. The required heater output rating is in watts per foot at 50 degree F.  (Heater selection based on -10 degree F ambient temperature.)

## Insulation Thickness on Metal Pipe

Pipe Size			1-inch fiberglass		2-inch fiberglass

2 inch or less			3 watt				 3 watt

2-1/2 inch to 4 inch		5 watt				 3 watt

5 inch to 6 inch			8 watt				 5 watt

  - The heater shall be XL-Trace as manufactured by Raychem Corporation.

  - Power connection, end seal, splice and tee kits components shall be applied in the field.

2.07	The system shall be controlled by an ambient sensing thermostat set at 40 degree F either directly or through an appropriate contactor.

PART III - EXECUTION

  - INSTALLATION

- Apply the heater linearly on the pipe after piping has been successfully pressure tested.  Secure the heater to piping with cable ties or fiberglass tape.

- Apply "electric traced" signs to the outside of the thermal insulation, or outside of jacket where piping is jacketed.

  - TESTS

After installation and before and after installing the thermal insulation, subject heat to testing using a 1000 VDC megger.  Minimum insulation resistance should be 20 to 1000 megaohms regardless of length.

# END OF SECTION