PART I - GENERAL

1.01	SCOPE OF WORK

- Work under this section includes all soil, waste, and vent piping inside the building as shown on plans.

PART II - PRODUCTS

  - SOIL AND WASTE PIPING

- Above grade and within buildings: "No-Hub" cast iron pipe and fittings.

- Below grade within building: "No Hub"  pipe and fittings.

- Below grade building exterior:  Bell and spigot cast iron pipe and fittings.

- Contractor may use PVC-DWV Schedule 40, ASTM 2665 piping for all soil and waste if allowed by local code. EXCEPTION:  Where piping penetrates rated wall, ceiling, floor, chase, etc., pipe must be cast iron at point of penetration.  Piping located in an HVAC return air plenum must be cast iron.

  - VENT PIPING

- Above and Below grade:  "No-Hub" cast iron pipe and fittings. Contractor may use pipe specified in 2.01-D. EXCEPTION:  Where piping penetrates rated wall, ceiling, floor, chase, etc., pipe must be cast iron.  Piping located in an HVAC return air plenum must be cast iron.

  - CLEANOUTS

- Cleanouts shall be as follows:

LOCATION			ZURN MODEL NUMBER

Finished floors			ZN-1400

Concealed risers		ZN-1469

Outdoors				ZN-1400

Horizontal pipe			ZN-1400

(above floor)

- Acceptable Manufacturers:  Zurn  (or approved equal).

  - Floor drains shall be per schedule on drawings.

- Acceptable Manufacturers:  Zurn or equal.

## PART III - EXECUTION

  - Soil and waste shall be uniformly graded to elevations shown.  If no elevations are given, they shall be pitched not less than 1/4" per foot for all pipes 2 1/2" in diameter and smaller and 1/8" per foot for pipes 3" and larger.

  - VENT PIPING

- Properly vent all fixtures as shown on the drawings. Project vents 12" above roof and install a flashing fitting approved by the roofing manufacturer.

- The heel of all vent stacks shall be flushed by the discharge of at least one fixture to prevent accumulation of rust and scale.  Branch vent lines below the highest fixture will not be permitted.

  - CLEANOUTS

- Cleanouts shall be provided at each change in direction of over 45 degrees, at the end of each soil or waste branch, at the base of each stack, and at least every 50 feet in all waste and soil lines or where indicated on drawings. Install wall cleanouts for horizontal vent lines below slab at point of rising in wall.

- Outdoors cleanouts shall terminate in a concrete block 18" X 18" by 6", flush with finish grade. Where concrete is in traffic area, reinforce concrete with #4 bars 6" on center each way.

  - Floor drains shall be of the same size as the pipe they are connected to.

  - Test all piping at no less than 10 feet of hydrostatic head for thirty minutes without lowering of the water level. Notify plumbing inspector and Engineer 48 hours in advance of when test is to take place.

  - No underground or concealed piping shall be covered prior to inspection by Engineer.

# END OF SECTION