PART I - GENERAL

  - DEFINITIONS:

Whenever occurring in Division 16000 the following words shall have the meanings given below:

- "Provide" shall mean to furnish, install and connect complete.

- "Wiring" shall mean wire or cable, installed in conduit, cable tray, or wireways with all required boxes, fittings, connectors, and accessories completely installed.

- "Work" shall be understood to mean the materials completely installed including the labor involved.

- "Plans and Specifications/Contract Documents” shall be understood to mean the complete documents, including all trades, divisions, sections, addenda, etc.

- "Review of Shop Drawings" - see Division 1.

- "Conduit" shall mean either rigid steel conduit, intermediate metal conduit (IMC), electrical metallic tubing (EMT), or plastic conduit (PVC).

  - The Contractor AGREES that upon the submittal of a bid, he will have read and studied ALL of the Contract Documents, and that all of the requirements and coordination resulting from these documents are included in his bid. The intent is to obtain a complete installation of electrical work to which end the Contractor shall provide ALL labor, equipment, material, freight, rigging, etc., specified, shown or scheduled on plans.  He also agrees that any other accessory items which may not be specified, shown, or scheduled on the plans, but which normally are furnished or can be reasonably implied from the specifications and/or plans to be required shall be provided.

  - No exclusion from, or limitations in the drawings, specifications, or other contract documents for the electrical work shall be reason for the omitting of the appurtenances or accessories necessary to complete any required system or item of equipment in this project.

  - Should the Contractor find any discrepancies and/or omissions in the contract documents, or be in doubt as to the intent of said documents, he shall obtain clarification or correction from the Architect and the Engineer BEFORE submitting a bid for work under this division. The Contractor will not be granted monetary allowances for discrepancies between his bid and the intent or the work after the contract is let, due to failure to follow this instruction.

  - The contractor shall not use any material or equipment that contains asbestos, PCB’s, or any other substance that is known to endanger the public health.

  - SCOPE OF WORK

- The Contractor shall refer to Architectural, Mechanical, and Structural drawings and Division 15 of these specifications for related work.

- The work of this division shall include the furnishing of all labor, supplies, materials, sales tax, permits, inspection fees, costs of testing, shop drawings, as built drawings, operation and maintenance manuals, and the performing of all operations including installation, cutting and chasing, trenching and backfilling, compaction, coordination with other trades on the job, etc., to the end of obtaining a complete installation of electrical work as shown on the drawings and called for in the written specifications.

- The work to be performed under the electrical contract shall include, but not be limited to:

- Service entrance conduit and wire.

- Service entrance equipment including disconnects, switchboards, panelboards, etc.

- Feeder conduit and wire.

- Distribution, lighting, and miscellaneous panelboards.

- Branch circuit conduit and wire.

- Lighting Fixtures.

- Wiring devices including receptacles, light switches, etc.

- Telephone service entrance conduit, and interior conduit and outlets.

- Fire Alarm System complete, if called for on the drawings

- Disconnects

- Control system conduit for mechanical contract.

- Provision of temporary power at 120/240, single phase for construction.

- Work not included under the electrical contract:

- Unless provided in motor control center, all motor starters and their associated control devices, heaters, etc. will be furnished with the motors under Division15 of these specifications.

- Control and interlock wiring for mechanical contract supplied systems.

- Telephone instruments and wiring

- Cable television equipment and wiring

- The owner will not make any consideration to the contractor for any alleged misunderstanding of the amount of work to be performed.  Submittal of a bid for work shall convey full agreement by the Contractor to all items and conditions specified, indicated on the drawings, and/or required by the nature of the job site.

- The Contractor shall be responsible for insuring that all equipment and materials are installed in a neat and workmanlike manner and are aligned, leveled and adjusted for satisfactory operation.  He shall install all equipment so that all parts are easily accessible for inspection, operation, maintenance and repair.  He shall insure that all equipment is solidly supported from building structures.

  - CODES, LAWS AND ORDINANCES

- Comply with all laws, codes, ordinances, and etc., having jurisdiction over the work to be performed under the contract for this project, EXCEPT where the requirements of the drawings and/or specifications are in excess of those called for in said laws, codes, ordinances, etc.

- Perform work in accordance with the standards listed below; EXCEPT where federal, state and/or local codes are more stringent, in which case, follow them instead:

- National Fire Protection Association			NFPA

- Underwriters Laboratories                          		UL

- American Society of Testing Materials              		ASTM

- National Electrical Code                           		NEC

- National Electrical Manufacturing Association      	NEMA

- Occupational Safety & Health Act                   		OSHA

- The Contractor shall be responsible for installation of the work called for in the contract documents in accordance with all codes, laws, and ordinances, which govern such work.  Should he encounter anything contained within the contract documents during preparation for bid which would prohibit the successful compliance of his responsibility under this item, he shall notify the Architect prior to execution of the contract for work so that adjustments can be made to the contract.

- The Contractor shall be responsible for obtaining all permits, inspection certificates, etc., required by local, state and/or federal authorities for this project, at his expense. Any and all additional work, expense, etc., incurred as the result of failure to request timely inspections, and or permits, shall be charged against the Contractor.

- Approval of the Architect, Engineer, and the appropriate inspection authorities must be secured for the complete electrical installation prior to contract closeout.  Upon completion of the electrical work, the Contractor will furnish the Architect with two (2) copies of all certificates of inspection, permits, etc.  Final payment to the Contractor will not be made until the requirements of this paragraph have been met.

  - LOCAL CONDITIONS

- Existing site utilities, underground services, structures, etc., are shown on the drawings accurately in scope only.  No expressed or implied guarantee is given as to exact location of the above items.  The Contractor is required to verify exact locations and subsequent effects of such on the job.

- The Contractor shall contact the local utility companies (power, telephone, etc.) to confirm the scheme of service called for on the drawings.  Should the Contractor discover the need for any change to these service schemes per the utility involved, he shall notify the Architect prior to execution of the contract so that a solution can be provided.  If any cost will be incurred to the project for any of the utilities to provide their services, the Contractor shall include this cost in the bid.  If the utility does not furnish this cost number to the Contractor prior to bid submittal, the Contractor shall include a letter with the bid submittal stating this fact.  This letter shall state that the cost will be forthcoming and will be an addition to the contract.

- Contractor shall verify with the Local Power Company the value of fault current in amperes which will be available at the secondary terminals of the Power Company transformer.  If this value is in excess of the AIC ratings of the various panels, circuit breakers, etc., as shown on the drawings, the Contractor shall supply such equipment with AIC ratings which will accommodate the available fault current.  Any increase in cost due to this item shall be included in the bid.

- Contractors desiring to bid on work under this division are required to visit the job site before bid submittal. During said visit the Contractor shall become familiar with all site conditions which will affect his work and the cost of the work.  He shall also verify exact location of the equipment of the various utility companies from whom services will be required.  The Contractor shall submit a letter with his bid stating that he has complied with this requirement.

  - PLANS AND SPECIFICATIONS

- While drawings are to scale, they are diagrammatic. DO NOT SCALE DRAWINGS HAVING 1/4" OR SMALLER SCALE.  Equipment, conduit, outlets, etc., are not exactly positioned; therefore, the Contractor shall refer to architectural drawings for actual building dimensions, ceiling layouts, light fixture locations, work by other trades, etc.

- Should any conflict exist between the drawings and the written specifications, the specifications shall generally govern.  Contact Engineer for clarifications.

- The drawings and written specifications for all divisions are part of the contract.  Any work and material shown in the one and omitted in the other, or which may be reasonably implied by both or either, shall be fully furnished and performed by the Contractor, as required for a complete electrical system installation.

- No deviation from the drawings and specifications shall be made without the full knowledge and consent of the Architect.  Should the Contractor find, at any time during the progress of the work, that, in his judgment, existing conditions make desirable a modification in requirements covering any particular item or items, he shall report such item promptly to the Architect for his decision and instructions.

- The right is reserved by the Architect to move any equipment, outlet, conduit, etc.; as much as ten (10) feet at no increase in cost, provided the Contractor is notified of the change before work on the detail in question is started.

- It shall be the responsibility of the Contractor to insure that the equipment he provides will fit into the available space, leaving reasonable space for maintenance and servicing of the equipment.  If, after the installation of any equipment, it is determined that the space requirements have not been met, the Contractor shall rearrange the work at no additional cost.

  - COORDINATION OF WORK

- It is the responsibility of the Contractor to plan all work so that it proceeds with a minimum of interference with all other trades.  He is to inform all parties concerned of openings in the building construction for equipment or conduit required for the electrical work. He is to coordinate the electrical work with the mechanical and plumbing installation.

- The contractor shall review and coordinate the locations of all electrical equipment (meters, instrument transformer cabinets, panels, disconnect switches, lighting contactors, etc.) mounted on the outside walls of buildings with the drawings for the mechanical, plumbing, and architectural disciplines to avoid any conflicts in locations with sprinkler risers, plumbing risers, rain downspouts, doors, etc.  Generally meter center risers are shown on the drawings for the purposes of information only; they are not dimensioned.  In addition, the locations of the meter centers on the site plans are diagrammatic only.  They are not dimensioned.  The contractor must coordinate these installations.  If there are any questions as to locations of equipment, notify the engineer for clarification prior to installation of equipment.

- The Contractor shall provide all required frames, sleeves, inserts, supports, anchor bolts, etc., as required for completion of the work.

- The Contractor shall lay out and coordinate all work well enough in advance so as to avoid conflicts or interference with other work in progress.  If there is any interference, the electrical layout may be altered to suit the conditions, prior to the installation of any work and at no additional cost to the Owner.  Consult the Architect for instructions.

- The contractor shall verify the location of all disconnect switches required by the project, prior to their installation.  The installed location of any disconnect shall not impede the access to, or working space around, any piece of equipment.  Neither shall the location cause any loss of equipment performance due to impeded air flow, etc. This requirement applies regardless of the location shown for the disconnects on the plans.  If there is any question as to disconnect location, the contractor shall ask the engineer for clarification prior to installation. If any disconnect is found to be installed in such a way that it causes any problems as mentioned above, it shall be relocated at the expense of the contractor.

- Work lines and established heights shall be in strict accordance with architectural drawings and specifications, insofar as these drawings and specifications extend.  It is the Contractor's responsibility to verify all elevations and detailed dimensions not indicated.

- The Contractor shall coordinate all outlets, fixtures, equipment, etc., with floor, wall and ceiling patterns. Any lines which must pitch shall have right-of-way over lines whose elevations can be changed.

  - EQUIPMENT DATA:

- Deliver all printed tags, instructions, certified drawings, parts lists, certificates, etc., supplied with equipment items, to the Architect at completion of the project.

- Assemble all such printed materials into a stiff-back binder identified on its face.  Provide quadruple copies.

  - SHOP DRAWINGS

- Shop drawings for switchboards, panelboards, transformers, generators, bus duct, cable tray, fire alarm systems, security systems, lighting fixtures, and other items as might be requested, shall be submitted to the Architect's Engineer for his approval, by the Contractor promptly upon receipt of the contract for work.

- The engineer will review the shop drawings for errors in the contractor’s interpretation of the contract documents only, and to assist the contractor in compliance with the documents.  Corrections of comments made on shop drawings during the review do not relieve the contractor from compliance with requirements of the contract documents, plans, and specifications.  Review of the shop drawings shall not relieve the contractor from responsibility for confirming and correlating all quantities and dimensions, coordination of his work with the other trades, and performance of his work in a safe and satisfactory manner.  Review of shop drawings shall not permit any deviations from plans and specifications by the contractor, nor shall it permit changes to the plans and specifications by the engineer.  Changes to, or deviations from, the contract documents may only be made by a Change Order issued by the Architect and executed properly.

- The contractor shall review the information prepared by his suppliers and note any changes required prior to submitting the information to the engineer and shall include the form, Exhibit 2, entitled “Certification of Compliance – Shop Drawings” with each submittal (see end of specifications).  Failure to complete and submit this form will result in rejection of the submittal without review.

- Equipment subject to shop drawing approval shall not be ordered until approved by the Engineer.  Material ordered or installed without such approval, if rejected by the Engineer, shall be removed and replaced with approved items at the Contractor's expense.

- In order to procure approval for such equipment, the Contractor shall submit a minimum of six (6) sets of shop drawings and/or brochures describing each piece of equipment.  Description shall include rated capacities, dimensions, manufacturer's catalog number, performance data with operating characteristics, optional features, modifications, etc.

- ALL BROCHURES AND DRAWINGS SHALL BE SUBMITTED AT THE SAME TIME. Items not approved shall be resubmitted with the necessary corrections made until final approval is obtained.

- See individual specification sections for additional shop drawing requirements.

- If equipment is substituted and approved in the shop drawing process; its use may affect electrical, mechanical, structural, and other systems which were designed based on the original equipment specifications.  Any changes, and their cost, in any of the divisions of work affected by the substitution of equipment, shall be the sole responsibility of the contractor making the substitution.

# PART II - PRODUCTS

2.01   MATERIALS AND EQUIPMENT

- All materials and equipment shall be new and the best grade.  They shall conform to all standards and requirements governing the work.  Any and all equipment and materials damaged during installation shall be immediately replaced at NO cost to the Owner.

- Reference shall be made to drawing schedules and details and/or specifications for manufacturer, model, catalog number, size, capacity, performance, installation, etc., of equipment and material.  Such information is used to denote design, workmanship, and quality desired.

- The Contractor shall offer his bid for work based on the electrical equipment (including light fixtures) which is described in these specifications and described in the respective schedules on the drawings.  Pre-bid approvals for substitute equipment will not be given.

- PRODUCT SELECTION PROCEDURES: Product selection shall be governed by the Contract Documents, and not by previous project experience which the Contractor or his suppliers may possess.  Procedures governing product selection include the following:

- PROPRIETARY SPECIFICATION REQUIREMENTS:  Where only a single product or manufacturer is named, provide the product indicated.  No substitutions shall be permitted.

- SEMIPROPRIETARY SPECIFICATION REQUIREMENTS:  Where two or more products or manufacturers are named, provide one of the products indicated.  No substitutions shall be permitted.

- NON-PROPRIETARY SPECIFICATONS:	  When the specification lists products or manufacturers that are available for incorporation into the work, but do not restrict the Contractor to use of these products only, the Contractor may propose any available product which complies with the contract requirements. Such products are still subject to the shop drawings submittal process.

- In the submission of substitute equipment and materials, the Contractor shall note the following: (1) capacities are absolute minimum and must be equaled, (2) physical size limitations for space allotted, (3) structural properties, (4) noise levels, (5) interchangeability, (6) compatibility with other materials, (7) similar items shall be same manufacturer and style wherever possible.

- All materials and equipment, for which a UL or NEMA standard is established, shall be so approved and labeled or stamped.

- NEMA standards shall be taken as minimum requirements for electrical equipment.

- Electrical equipment shall operate properly under a 10 percent plus or minus voltage variation.

- Adhesives are not acceptable as mounting, supporting or assembling media.

PART III - EXECUTION

  - All materials required for the project shall be ordered by the Contractor in a timely manner which allows the material to be received at the job site for installation in agreement with the job schedule, so that work of the other divisions is not held up in any way.

  - All materials and equipment received at the job site by the Contractor shall be stored and protected from damage while they wait to be installed.

  - All work shall be carried out in a neat and orderly manner by experienced electricians, under the constant supervision of a competent electrician, trained and licensed in this field, who shall represent the Contractor at all times in connection with the work.

  - Materials or work installed, rejected by the Architect's Engineer upon inspection shall be completely removed by the Contractor, and the work redone in a manner acceptable to the Engineer by the Contractor at no charge.

  - When rejected work is removed, should other material, equipment, etc., be damaged in the process, the Contractor shall make all necessary repairs, so that the damaged equipment is equal in quality, strength and appearance to its original state.

  - SPACE REQUIREMENTS:

- The Contractor is fully responsible for determining in advance of purchase that all equipment and materials proposed for installation will fit into the space indicated while allowing sufficient clearance about the equipment and materials to allow proper maintenance and servicing of all components requiring such, including equipment and materials of other divisions located in the vicinity.

- Clearances in front of panelboards, switchboards, motor starters, busway taps, and other electrical equipment requiring servicing while energized, shall be provided in accordance with the NEC, table 110-16a, as required by the code text.

- The contractor shall prepare, and submit for review and approval prior to ordering equipment, dimensioned rough-in drawings at ½” = 1’-0” scale for each equipment room and meter equipment layout.  These drawings shall show all equipment to scale based on the actual equipment ordered and shall be fully dimensioned.

  - FIRESTOPPING:

- Firestop all penetrations of building fire rated surfaces made by this division.

- Each penetration shall be protected by a firestop system with a rating equal to or greater than the original assembly in which the penetration occurs.

- All firestop material shall be installed in accordance with manufacturer’s standard details and the UL Building Materials Directory for each type of fire rated assembly penetrated.

- Telephone sleeves shall be firestopped with materials that will permit re-entry and use of the sleeves.

  - WIRING ELECTRICALLY OPERATED EQUIPMENT:

- The Contractor shall provide all conduit, conductors, wiring, etc., required to connect power to all electrically operated equipment installed on the project, whether provided by this division or other divisions, or by the owner.

- The Contractor shall install, support, and electrically connect motor starters, disconnects, etc., and shall complete all power wiring circuits so that each is left in satisfactory condition.

- All control equipment associated with any equipment furnished under any other division, or by the owner, shall be furnished by that provider.

- This division shall provide all conduit required for control wiring as needed for Division 15000.  Refer to that division and its associated drawings for specifics.

- This division is responsible for the provision of, and fire alarm system wiring of, duct smoke detectors for all HVAC equipment requiring them.  If there is a fire alarm system provided for the project, the detectors shall be tied to that system.  If there is no fire alarm system, the Contractor shall provide remote visual and audible alarm indicators per the requirements of NFPA 90A, latest edition.

  - RECORD AND AS-BUILT DOCUMETS:

- The Contractor shall maintain at the job site a complete set of Contract Documents. These documents shall be kept current with all changes, substitutions, etc., to the original documents as reflected by the actual work being installed.

- At closeout, the Contractor shall provide the Owner with one complete set of as-built reproducible drawings, and two clean sets of complete specifications.  These documents shall show installed locations, sizes, etc., of all work and material as required by the contract documents and actually installed on the project.

- For each piece of equipment installed or provided, the Contractor shall provide three (3) sets of:

- Manufacturer’s printed catalog pages

- Manufacturer’s operating and maintenance instructions

- Manufacturer’s wiring and connection diagrams, etc.,

- Motor interlock and control diagrams, showing operating instructions for, and normal positions of, each motor and controller

All of this information shall be provided in bound 8-1/2” by 11” hardback booklets.

  - CLEANING:

- The Contractor shall insure that all interior and exterior surfaces of panelboards, transformers, switchboards, motor starters, cabinets, etc., are cleaned so as to be free of dust, dirt, grease, plaster, debris, etc.  Lighting fixtures shall be cleaned according to manufacturer’s recommendations.

- Any electrical equipment having sustained damage to any factory painted surfaces shall have that damage repaired and restored to original factory condition.

- Any and all ferrous metal surfaces exposed on the electrical system shall be painted.

  - TEMPORARY LIGHTING AND POWER:

- As soon as is possible, the Contractor shall install temporary electrical wiring and lighting for the project in accordance with NEC Article 305.

- Wiring shall consist of non-metallic sheathed cable with ground wire.

  - EXCAVATION, SHORING, AND BACKFILL:

- The Contractor shall perform all necessary excavation required for installation of his work.  Each utility shall be installed in a separate trench.

- Excavation shall be below that required for general construction and final grade.  It is expected that the Contractor shall process normally difficulties encountered in excavation related to rocks, debris, etc.  However, should the Contractor encounter “solid” rock impediments to his excavation, he shall contact the Architect for directions.

- Any and all trenching shall be performed strictly in accordance with OSHA, and other authorities having jurisdiction, rules and regulations regarding “cave in” safety shoring.  All shoring material used shall be completely removed prior to backfilling the trench.

- The Contractor shall not backfill trenches until the conduit banks have been inspected by the proper authorities.

- Backfill shall be done simultaneously on both sides of the equipment, raceways, etc.

Backfill shall be clean soil, free of rocks, cinders, wood, debris, etc.

- Backfill shall be installed in 12-inch layers.  It shall be compacted to 85% per ASTM D-1557 in areas under sidewalks and grass; and to 95% under any paved areas.

- Should concrete encasement of raceways be required, the sides and floor of the trench shall be used as formwork for the concrete.  This shall not apply unless the excavation is clean, free of debris, and of the proper size.

  - CUTTING AND PATCHING:

- The Contractor shall be responsible for the location and size of all openings required for his work.

- The Contractor shall not cut into structural members or architectural finish surfaces without expressed written approval of the Architect.

- Any patching of surfaces required by the Contractor’s work shall be made so that they are equal in quality and appearance to the original surface.

  - FLASHING:

- Raceways which pass through walls or roof surfaces to the outside shall be flashed in accordance with architectural standards and with the requirements of the roofing manufacturer.

- Any raceways penetrating the roof shall maintain a clearance of 18 inches minimum from all parapets.

- Whenever raceways pass through floor structures which contain a water proofing membrane, the Contractor shall provide a watertight floor sleeve for each raceway.  The lowest floor shall be exempt.

  - MOISTURE - DAMP PROTECTION:

A.	Whenever any electrical component such as panels, raceways, etc., will be in contact with surfaces which may become damp or wet, that component shall be mounted on standoff devices so that it is a minimum of ¼” away from the surface.

  - GUARANTEE AND WARRANTY:

- The Contractor and the General Contractor shall, and hereby does, guarantee that all work executed, and all electrical equipment installed, under this division will be free of all defects in materials, manufacture, and workmanship for a period of one (1) year from the date of final acceptance of the building.  The above parties agree that they will, at their expense, repair and/or replace all such defective work and equipment, and any and all other work damaged thereby, which becomes defective during the term of this guarantee.

## END OF SECTION