PART I - GENERAL

  - The Contractor shall insure that all parts of any and all electrical installations which either enclose or guard live parts shall be solidly grounded

  - All work performed under this Division shall meet the grounding requirements of the NEC, Article 250.

### PART II - PRODUCTS

  - CONDUCTORS:

- All grounding conductors shall be copper.  Conductors smaller than No. 8 AWG shall be solid; all other conductors shall be stranded.  Ground conductors shall be bare or have type THHN insulation, green in color.

- Aluminum grounding conductors are strictly prohibited.

- Service entrance grounding electrode conductors shall be sized per the NEC, Article 250, and table # 250-94.

- Equipment grounding conductors shall be sized per the NEC, Article 250, and table # 250-95.

  - GROUND RODS:

- Ground rods shall be copper clad, sectional, solid steel.  Rods shall be 10-ft. long, ¾ in. diameter.  Rods shall be sectional, threaded on both ends to be used if depths of more that 10 feet are required to achieve desired ground resistance value of 5 ohms.  All couplings shall be bronze made by the rod manufacturer.  Rods shall be as manufactured by the Copperweld Steel Company.

  - CONNECTIONS:

- Grounding connections made to ground rods, building re-steel, or counterpoise systems shall be made with the Cadweld process.

- Grounding connections to water pipes shall be made with clamps intended for the purpose such as Burndy type GAR clamps.

- Grounding connections to boxes, fixtures, etc. shall be made at the factory provided grounding lug.

PART III - EXECUTION

  - The Contractor shall provide grounds to all equipment requiring them, including, but not limited to:

- Electric service

- Secondary of transformers (except the isolating type).

- Conduit and enclosures.

- All neutral conductors.

- Panelboards, switchboards, etc.

- Ground terminals on receptacles, appliances, equipment, etc.

  - In all conduit systems the Contractor shall provide a separate green grounding conductor, in addition to the circuit neutral, inside the raceway with the phase conductors.

  - The Contractor shall, unless otherwise noted, use the cold water piping system along with two 3/4" copperweld ground rods, driven to a depth to provide a maximum of 5 ohms ground resistance, as the grounding electrodes for the electrical system.  The grounding conductor that connects the electrical system to the ground electrode shall be sized per the NEC table 250-94.  The ground rods and the grounding conductor shall be attached to the same physical point on the water pipe.  Two bolt style, split, wrap around ground clamps shall be used to clamp conductor to water pipe.  The Contractor shall connect the copper grounding conductor to the main panel device, i.e., panelboard, switchboard, etc.; and shall connect it to the system neutral at this point. Shunt connections across valves and water meter shall be provided.

  - When the water system is nonmetallic pipe, then the ground system shall consist of a minimum of three (3) ground rods spaced 10'-0" apart minimum.  Tops of rods to be placed a minimum of 12” below the surface of the ground.

  - When equipment is subjected to vibration, when flexible conduit is used, and when surface raceways are used, the Contractor shall connect the equipment ground terminal to the rigid conduit system by means of a ground wire.

  - The neutral of all dry type transformers shall be grounded to building steel or cold water pipe.  All such connections shall be made in a physical building space where damage to the connection is not likely.

## END OF SECTION