PART I - GENERAL

  - The Contractor shall insure that all electrical equipment is properly and visually marked as to function, voltage, etc.

  - All General and Supplementary Conditions and General Requirements (Division 1) shall apply to the work specified in this section.

PART II - PRODUCTS

  - MATERIALS:

- Conduit and raceway labeling shall be with stenciled letters of height of 2 conduit diameters, or 2 inches, which ever is smaller.  Voltage and function shall be stated in label.

- Label paint shall be:

- 480/277 volt raceway – Red paint

- 208/120 volt raceway – Black paint

- 240/120 volt raceway – Blue paint

- Equipment and cabinet labeling shall be done with plastic plates of sandwich type materials with the inner material being white in color.  All such plates are to be attached to the cabinets or equipment with screws.  Plates shall state equipment or cabinet name, voltage, phase, and date installed.  Plate outer plastic colors shall be:

- 480/120 volt equipment – Red plastic with white letters

- 208/120 volt equipment – Black plastic with white letters

- 240/120 volt equipment – Blue plastic with white letters

All lettering is to be made by machine engraving which cuts through the outer colored plastic plate to reveal white color letters with letter height of 3/8”.

- Planelboards and switchboards shall be provided with circuit directories of white heavy paper cards.  Schedules shall be type written in black ink.

PART III - EXECUTION

  - The Contractor shall provide labels for all electrical panels, switchboards, disconnects, cabinets, feeder and service raceways, motors, and major pieces of electrical equipment installed under this division.

  - Each panelboard shall be provided with a typewritten directory card of all circuits in the panel.

  - Each circuit breaker in all switchboards shall be labeled as to what it feeds.  All breakers shall have their ampacity clearly marked on the breaker.

  - Underground outside conduit runs shall be marked.  Markers shall consist of 4” by 4” by 18” long concrete stakes located above the conduit at ends and corners.  Install stakes flush with finished grade.

  - All feeder raceways shall be labeled by stenciling at intervals not to exceed 50 feet along the entire length of the raceways where they are exposed.

# END OF SECTION